## Revision Control
Aquantis C-Plane System Requirements Document (SRD)
Draft - Work in Progress
Revision Log
Revision | Date | Author | Revised Content
Aquantis SRD_KG_Rev_6-Feb-13.xlsx | 2013-02-06 | Ken Gluck | Added revised "Florida Current Design Considerations" table to "Environmental Conditions (2.4MW)" tab
Aquantis SRD_KG_Rev_8-Feb-13.xlsx | 2013-02-08 | Ken Gluck | Added "Revision Control" tab

## Top Level Requirements (2.4MW)
Draft - Work in Progress
Target Cost of Energy | 8c/kWh
CAPEX | All components within given CAPEX budget
Reliability
Design Life | 20 years
Maintenance Interval | 5 years
Nacelle Environment | Dry
Energy Production
C-Plane Rated Output | 2.4 MW
Target Capacity Factor | 65%
Rated Current Speed | 1.6m/s
Installation and Maintenance
Method of Transport | ####
Net Buoyancy | ####
Pitch Angle for Towing and Operation | ####
Site Aspects
Operating Minimum Depth | 70m
Operating Maximum Depth | 200m
Crush Depth | 305m
Certification | C-Plane shall be certifiable, all parts shall be designed and built according to applicable standards

## Environmental Conditions(2.4MW)
Environmental Conditions and Loads | Draft - Work in Progress
Seabed Depth | 300 - 400m
Distance to Shore along Cable Route | 13 - 16 km
Operation
Mean current heading @70m | 14°N
Design current @70m | 1.6m/s
Min speed @70m | 0.1m/s
Max speed at hub height | 1.8m/s
Max speed at blade tip | 2.0m/s
Installation
Max wave height during towing | 1m
Max current speed during towing | 1.75m/s
Survivability
100 year return wave conditions | Hs = 12m, Tp = 12-20s
100 year orbital velocities | 0.8-1.15m/s @50m
0.44-0.93m/s @70m
0.24-0.75m/s @90m
Extreme current heading @70m | 80°
Associated speed at extreme current heading | 0.25m/s
Number of fatigue cycles | 113 million wing pass cycles (for two bladed rotor at 5.37 rpm)
Florida Current Design Considerations
** UNDER REVIEW ** INCORPORATE WORST CASES FOR FATIGUE & STABILITY
Concern in Fl Current | Cause | Length Scale | Speeds | Period | Comments
Seasonal Upwelling, downwelling; surface cooling | Upwelling in trough of frontal eddies, lifts the density structure of the front in upper 200m; Surface cooling due to passage of cold atmospheric fronts | Amplitude = 10m | 10m/day | day | Buoyancy loads of ~30N/m3 due to upwelling
Continental Shelf waves | Wind induced | 100km [1] | 28cm/s [1] | 4days [1] | Seasonal winds cause subinertial frequency oscillations in sea level, upwelling/downwelling, flow over topography generates north/south along FL coast [1]. Not likely to be of great concern at offshore location
|  | 200km [1] | 15cm/s [1] | 14days [1]
Internal waves – baroclinic inflection points | Interaction of barotropic and internal tides with self edge and along-shelf topography; FC instabilities; passage of frontal eddies; estuaries | Amplitude: 1-20m; depends on frequency [Sutherland et al., 2000] | 10-20 cm/s [13] | 30min [6] | Buoyancy loads of ~30N/m3 due to upwelling maybe expected; activity dominant during summer; solitary wave observational data lacking
Typical period 5-10 min[13]
Min. period = 10s. [9]
Max period = 24hrs [Beal]
Inertial and Low frequency Oscillations | Inertial motion of the ocean and internal tides; cause for 10hr oscillation unknown | Low frequency ~ 10 – 50 km Hz scale; 10m vertical scale | ~1m/s to +/ 0.5 m/s | 27, 12.4 and 10 hrs | Not of great concern [15], except if western edge of Current is east of turbine system when flow reversals of ~+/ 0.5 m/s may occur
10hr signal: barotropic 10s of meters in vertical scale
Surface Waves | Winds particularly during hurricanes | Maximum wave ht recorded 7m | 10cm/s at 50m depth | 7-8 s wave period | Not of great concern for systems at >100m depth
Meanders | Primarily barotropic instabilities | λ=100-250km [3] | 40 cm/s [3] | 2-14 days [3] | May brings western edge of Current in proximity of system, exacerbating flow fluctuations due to shear-layer instability, spin-off eddies – then becomes a stability concern; Dynamic forces of ~300 N/m2 ; Extent of meanders in region need to be determined
|  | λ=160-240km [16] | 50 cm/s [16] | 4-6 days [16]
|  | λ=340km [2] | 30cm/s [2] | 12, 5 days [2]
|  | λ=170km [2] | 40cm/s [2] | 12, 5 days [2]
|  | Amp = 5km [16] | - | -
Eddies | Meander in current causes spin-offs at outer edges of core, Can occur from generation in Loop Current, baroclinic instabilities; D=meander amplitude, varies depending on bathymetry | - | 50cm/s [6] | 11 hrs [6] | Will give rise to fluctuations in local flow velocities: dynamic forces ~ +/- 300N/m2;
|  | D=10-30km, λ=75-122km, d=200m [3] Miami | - | - | Buoyancy loads of ~30N/m3 due to upwelling; Need further observational data on TKE dissipation rates during passage
|  | D = 23km, L = 34km [16] | 39cm/s [16] | 2.2 days [16]
|  | Spin-Offs, D=10km, L=20-50km [2] | 25cm/s[8] | Interval 1-2days [8]
Height H = 400m
Storm surge (12m – 100yr return period) | Hurricane | λ=3m [7] | .05m/s [7] | Seconds to minutes [7] | Max directionally-fluctuating dynamic forces at 100-200m depth: 20kN/m2; impulsive forces from turbulent gusts; additional observational/modeling information needed; 1Hz sampling during episodic events to identify TKE dissipation rates
|  | λ=100m [7] | 1-2m/s [7] | Seconds to minutes [7]

## Derived Requirements (2.4MW)
Draft - Work in Progress
Requirement ID | Top Level Requirement | Derived Requirement | Relevant to | Group | Loads / Information / Reference
B1 | Components within CAPEX budget | Blades target cost: $### | Blades | Platform
B2 | C-Plane Rated Output: 2.4MW | Rotor output at rated speed: 1412kW | Blades | Platform
B3 | Design Life: 20 years | Survive extreme flow velocity: 2.0m/s | Blades | Platform
B4 | Design Life: 20 years | Survive extreme flow shear: 0.01 mps/m | Blades | Platform
B5 | Design Life: 20 years | Survive 100-year return wave loading | Blades | Platform
B6 | Design Life: 20 years | Survive 56.5 million wing pass cycles | Blades | Platform
B7 | Maintenance Interval: 5 years | Blades shall require no maintenance in 5 year interval | Blades | Platform
B8 | Pitch Angle for Towing and Operation: ### | Blades shall be neutrally buoyant | Blades | Platform
B9 | C-Plane shall be certifiable | Blades shall be designed and built according to relevant standards | Blades | Platform
RH1 | Components within CAPEX budget | Rotor Hub target cost: $### | Rotor Hub | Platform
RH2 | C-Plane Rated Output: 2.4MW | Rotor output at rated speed: 1412kW | Rotor Hub | Platform
RH3 | Design Life: 20 years | Survive extreme flow velocity: 1.8m/s | Rotor Hub | Platform
RH4 | Design Life: 20 years | Survive extreme flow shear: 0.01 mps/m | Rotor Hub | Platform
RH5 | Design Life: 20 years | Survive all loads imparted by blades over lifetime | Rotor Hub | Platform
RH6 | Maintenance Interval: 5 years | Rotor Hub shall require no maintenance in 5 year intervals | Rotor Hub | Platform
RH7 | Pitch Angle for Towing and Operation: ### | Rotor Hub shall be neutrally buoyant | Rotor Hub | Platform
RH8 | C-Plane shall be certifiable | Rotor Hub shall be designed and built according to relevant standards | Rotor Hub | Platform
T1 | Components within CAPEX budget | Truss target cost: $### | Truss | Platform
T2 | Design Life: 20 years | Survive extreme flow velocity: 1.8m/s | Truss | Platform
T3 | Design Life: 20 years | Survive extreme flow shear: 0.01 mps/m | Truss | Platform
T4 | Design Life: 20 years | Survive 100-year return wave loading | Truss | Platform
T5 | Design Life: 20 years | Survive 113 million wing pass cycles | Truss | Platform
T6 | Maintenance Interval: 5 years | Truss shall require no maintenance in 5 year intervals | Truss | Platform
T7 | Net buoyancy: ###kN | Truss target buoyancy: ###kN | Truss | Platform
T8 | Pitch Angle for Towing and Operation: 0° | Truss shall maintain level position in speed range 0m/s to 1.6m/s | Truss | Platform
T9 | Pitch Angle for Towing and Operation: 0° | Truss shall drive C-Plane down at speeds over 1.6m/s | Truss | Platform
T10 | C-Plane shall be certifiable | Truss shall be designed and built according to relevant standards | Truss | Platform
N1 | Components within CAPEX budget | Nacelle target cost: $### | Nacelle | Platform
N2 | Design Life: 20 years | Survive extreme flow velocity: 1.8m/s | Nacelle | Platform
N3 | Design Life: 20 years | Survive extreme flow shear: 0.01 mps/m | Nacelle | Platform
N4 | Design Life: 20 years | Survive 100-year return wave loading | Nacelle | Platform
N5 | Design Life: 20 years | Survive 113 million wing pass cycles | Nacelle | Platform
N6 | Maintenance Interval: 5 years | Nacelle shall require no maintenance in 5 year intervals | Nacelle | Platform
N7 | Net buoyancy: ###kN | Nacelle target buoyancy: ###kN | Nacelle | Platform
N8 | Dry Environment Inside Nacelle | No leakage during lifetime | Nacelle | Platform
N9 | Dry Environment Inside Nacelle | Nacelle shall operate as pressure vessel up to maximum depth | Nacelle | Platform
N10 | C-Plane shall be certifiable | Nacelle shall be designed and built according to relevant standards | Nacelle | Platform
M1 | Components within CAPEX budget | Mooring system target cost: $### | Moorings | Moorings & Stabiltiy
M2 | Maintenance Interval: 5 years | Moorings shall not require any inspection during 5 year intervals | Moorings | Moorings & Stabiltiy
M3 | Operating Depth Range: 70 - 200m | Moorings shall restrict C-Plane to 70m below surface at hub height | Moorings | Moorings & Stabiltiy
M4 | Design Life: 20 years | Survive extreme flow velocity: 1.8m/s | Moorings | Moorings & Stabiltiy
M5 | Design Life: 20 years | Survive maximum dynamic loads due to platform accelerations | Moorings | Moorings & Stabiltiy
M6 | Design Life: 20 years | Survive 100-year return wave loading | Moorings | Moorings & Stabiltiy
M7 | Design Life: 20 years | Survive all cyclic loading due to platform behavior | Moorings | Moorings & Stabiltiy
M8 | Design Life: 20 years | Survive all cyclic loading due to Vortex Induced Vibrations | Moorings | Moorings & Stabiltiy
M9 | Design Life: 20 years | Anchors shall maintain position with worst combination of thrust and uplift | Moorings | Moorings & Stabiltiy
M10 | C-Plane shall be certifiable | Mooring system shall be designed and built according to relevant standards | Moorings | Moorings & Stabiltiy
S1 | Components within CAPEX budget | Installation target cost: $### | Stability, Transport & Installation | Moorings & Stabiltiy
S2 | Pitch Angle for Towing and Operation: 0° | Towing arrangement to be designed for zero pitch of C-Plane | Stability, Transport & Installation | Moorings & Stabiltiy
S3 | Design Life: 20 years | Accelerations during transportation to be within limits from internal equipment and structures | Stability, Transport & Installation | Moorings & Stabiltiy
S4 | Design Life: 20 years | Accelerations during operation to be within limits from internal equipment and structures | Stability, Transport & Installation | Moorings & Stabiltiy
S5 | Design Life: 20 years | C-Plane should not be inverted at any time | Stability, Transport & Installation | Moorings & Stabiltiy
S6 | C-Plane shall be certifiable | Marine operations shall be planned and executed according to relevant rules and standards | Stability, Transport & Installation | Moorings & Stabiltiy
BE1 | Components within CAPEX budget | Bearings and seal target cost: $### | Bearings | Drivetrain
BE2 | Maintenance Interval: 5 years | Bearings shall continue to operate without maintenance for 5 years | Bearings | Drivetrain
BE3 | Design Life: 20 years | Survive extreme flow velocity: 1.8m/s | Bearings | Drivetrain
BE4 | Design Life: 20 years | Survive extreme flow shear: 0.01 mps/m | Bearings | Drivetrain
BE5 | Design Life: 20 years | Survive 113 million wing pass cycles | Bearings | Drivetrain
BE6 | Dry Environment Inside Nacelle | Bearings shall maintain shaft displacement within seal limitations | Bearings | Drivetrain
BE7 | C-Plane Rated Output: 2.4MW | Maximum losses in bearings at rated speed: 1% | Bearings | Drivetrain
BE8 | C-Plane shall be certifiable | Bearings shall be designed and built according to relevant standards | Bearings | Drivetrain
SE1 | Maintenance Interval: 5 years | Seal shall continue to operate without maintenance for 5 years | Seal | Drivetrain
SE2 | Design Life: 20 years | Seal travel: 56.5 million shaft revolutions | Seal | Drivetrain
SE3 | Dry Environment Inside Nacelle | Seal leak rate shall not exceed bilge system capacity | Seal | Drivetrain
SE4 | Operating Depth Range: 70 - 200m | Seal shall not leak excessively in speed range 0-10rpm | Seal | Drivetrain
SE5 | Crush depth: 305m | Seal shall not leak excessively at 0rpm | Seal | Drivetrain
SE6 | C-Plane shall be certifiable | Seal shall be designed and built according to relevant standards | Seal | Drivetrain
MB1 | Maintenance Interval: 5 years | Brake shall continue to operate without maintenance for 5 years | Mechanical Brake | Drivetrain
MB2 | Maintenance Interval: 5 years | Brake shall supply wear signal to control system | Mechanical Brake | Drivetrain
MB3 | Design Life: 20 years | Brake shall be capable of stopping turbine in 2.0m/s flow velocity | Mechanical Brake | Drivetrain
MB4 | Design Life: 20 years | Brake shall be engaged when turbine is stopped for maitnenance | Mechanical Brake | Drivetrain
MB5 | Design Life: 20 years | Brake shall not fail on demand | Mechanical Brake | Drivetrain
MB6 | Design Life: 20 years | Brake shall automatically engage in event of loss of hydraulic pressure | Mechanical Brake | Drivetrain
MB7 | C-Plane shall be certifiable | Brake shall be designed and built according to relevant standards | Mechanical Brake | Drivetrain
H1 | Components within CAPEX budget | Hydraulic system target cost: $### per drivetrain | Hydraulics | Drivetrain
H2 | Maintenance Interval: 5 years | Hydraulic system shall continue to operate without maintenance for 5 years | Hydraulics | Drivetrain
H3 | Design Life: 20 years | Hydraulic system shall survive 20 years inside nacelle atmosphere | Hydraulics | Drivetrain
H4 | Design Life: 20 years | Hydraulic system shall survive defined duty cycle | Hydraulics | Drivetrain
H5 | Design Life: 20 years | Hydraulic system shall have capacity to brake turbine at 1.8m/s | Hydraulics | Drivetrain
H6 | Design Life: 20 years | Hydraulic system maximum pressure: 420 Mpa | Hydraulics | Drivetrain
H7 | C-Plane Rated Output: 2.4MW | Maximum losses in hydraulic system at rated speed: 10% | Hydraulics | Drivetrain
H8 | C-Plane shall be certifiable | Hydraulic system shall be designed and built according to relevant standards | Hydraulics | Drivetrain
GE1 | Components within CAPEX budget | Generator target cost: $### | Generator and Electrical | Drivetrain
GE2 | Components within CAPEX budget | Transformer target cost: $### | Generator and Electrical | Drivetrain
GE3 | Maintenance Interval: 5 years | Generator shall continue to operate without maintenance for 5 years | Generator and Electrical | Drivetrain
GE4 | Design Life: 20 years | Generator shall survive 20 years inside nacelle atmosphere | Generator and Electrical | Drivetrain
GE5 | Design Life: 20 years | Generator shall operate continuously throughout lifetime | Generator and Electrical | Drivetrain
GE6 | C-Plane Rated Output: 2.4MW | Maximum losses in generator at rated speed: 3% | Generator and Electrical | Drivetrain
GE7 | C-Plane shall be certifiable | Generator and electrical system shall be designed and built according to relevant standards | Generator and Electrical | Drivetrain
HE1 | Components within CAPEX budget | Heat Exchanger target cost: $### | Heat Exchanger | Drivetrain
HE2 | Maintenance Interval: 5 years | Heat Exchanger shall continue to operate without maintenance for 5 years | Heat Exchanger | Drivetrain
HE3 | Design Life: 20 years | Heat Exchanger shall have capacity for ### kW of cooling throughout lifetime | Heat Exchanger | Drivetrain
HE4 | C-Plane shall be certifiable | Heat Exchanger shall be designed and built according to relevant standards | Heat Exchanger | Drivetrain
GC1 | Components within CAPEX budget | Grid Connection target cost: $### | Grid Connection | Drivetrain
GC2 | Design Life: 20 years | Dynamic cable shall survive 100-year return loading at any point in lifetime | Grid Connection | Drivetrain
GC3 | Design Life: 20 years | Dynamic cable shall survive all fatigue loading over lifetime | Grid Connection | Drivetrain
GC4 | Design Life: 20 years | Dynamic cable shall not be load bearing in any C-Plane position | Grid Connection | Drivetrain
GC5 | C-Plane Rated Output: 2.4MW | Grid connection shall be rated for continuous ###MW transmission | Grid Connection | Drivetrain
GC6 | C-Plane Rated Output: 2.4MW | Grid connection maximum losses: 2% | Grid Connection | Drivetrain
GC7 | C-Plane shall be certifiable | Grid connection shall be designed and built according to relevant standards | Grid Connection | Drivetrain

## Design Load Cases (2.4MW)
Draft - Work in Progress
Load Case ID | Condition | Load Case Description | Loads to be defined
1 | Transport and Installation | Towing C-Plane to site | Loads due to waves, towing speed, loads at attachment points, accelerations and inclinations during towing
2 | Transport and Installation | Lowering C-Plane to operating position | Loads due to waves, loads at attachment points, accelerations and inclinations
3 | Transport and Installation | Raising C-Plane to surface | Loads due to waves, loads at attachment points, accelerations and inclinations
4 | Operation | Fatigue cycles: 113 million blade passing cycles at 5.37 rpm
5 | Operation | Braking at 1.8m/s | Braking torques, resultant thrust and moment on blades
6 | Operation | 100-year return environmental loads | Resultant current velocities including orbital velocities
7 | Accidental | Failure of one mooring line or anchor | Maximum uplift and thrust conditions from C-Plane
8 | Accidental | Hydraulic failure
9 | Accidental | Electrical failure
10 | Accidental | Braking of one rotor | Unbalanced forces on C-Plane