## Data Rights Notice
PROTECTED RIGHTS NOTICE
These protected data were produced under agreement no. DE-EE0007347 with the U.S. Department of Energy and may not be published, disseminated, or disclosed to others outside the Government until five (5) years from the date the data were first produced, unless express written authorization is obtained from the recipient. Upon expiration of the period of protection set forth in this Notice, the Government shall have unlimited rights in this data. This Notice shall be marked on any reproduction of this data, in whole or in part.

## 0400 SCADA
[13 empty] | Risk Ranking | [10 empty] | Updated Risk Ranking | [11 empty] | 2nd Updated Risk Ranking
0400 SCADA FMECA Table | [13 empty] | Severity Class |  |  |  | Risk Class | [6 empty] | Severity Class |  |  |  | Risk Class | [7 empty] | Severity Class |  |  |  | Risk Class
Risk ID | Item Description | Function | Tech. Class | Novel Aspects | Failure Mode | Failure Effects (Local, WEC, System) | Failure Cause(s) | Initial Mode of Operation | Risk Reduction Design | Preventative Detection | Post Failure Detection | Post Failure Repair Strategy (automated, manual) | Occurrence | Human Safety | Environment | Operation | Assets | Human Safety | Environment | Operation | Assets | Responsible Party | Actions Taken | Occurrence | Human Safety | Environment | Operation | Assets | Human Safety | Environment | Operation | Assets | 2nd Recommended Actions | Responsible Party (2nd) | Actions Taken (2nd) | Occurrence | Human Safety | Environment | Operation | Assets | Human Safety | Environment | Operation | Assets | Status (open or closed) | Notes
400-1 | SCADA components | Control and data collection | 1 | none | Fire/smoke | 1) Power loss due to short 2) Damage to SCADA system | Electrical short or internal component failure | Normal | 1) All SCADA functions are redundant on alternate side 2) Airtight enclosures 3) Low power 4) In cabinet fire suppression | 1) Fire/smoke alarm | 1) Enclosure fire alarm 2) Enclosure temperature 3) Visible and IR camera | Manual in-situ repair and inspection | 5 | 1 | 1 | 6 | 5 | Low | Low | Low | Low
410-1 | Single PTO tape scale encoder | Provide position feedback to drives | 2 | new environment | Signal failure | 1) Single encoder fail 2) Loss of position feedback | Wiring Issue - unknown internal fault - unknown poor solder joint - wire chaffe due to improper routing | Normal | 1) V&V 2) Redundant encoders | 1) None | 1) Encoder data | Manual switch of encoders onboard Programmatically selected encoders from internal system comparison. | 7 | 1 | 1 | 2 | 4 | Low | Low | Low | Low | [24 empty] | Can signals be multiplexed and switched remotely? - Yes, internal comparison can be performed of all encoders and they can be switched automatically or manually remotely.
410-2 | Single PTO tape scale encoder | Provide position feedback to drives | 2 | new environment | Signal failure | 1) Single encoder fail 2) Loss of position feedback | Corrosion induced failure | Normal | 1) Material selection 2) IP 67 3) Climate Control 4) Redundant encoders | 1) None | 1) Encoder data | Manual switch of encoders onboard Programmatically selected encoders from internal system comparison. | 6 | 1 | 1 | 2 | 4 | Low | Low | Low | Low | [24 empty] | Reduced Severity Class of Operation due to having redundant encoders in design.
410-2 | Single PTO tape scale encoder | Provide position feedback to drives | 2 | new environment | Signal failure | 1) Single encoder fail 2) Loss of position feedback | Contamination induced failure | Normal | 1) Thorough cleaning at commissioning 2) Redundant encoders | 1) None | 1) Encoder data | Manual switch of encoders onboard Programmatically selected encoders from internal system comparison. | 7 | 1 | 1 | 2 | 4 | Low | Low | Low | Low | [24 empty] | Reduced Severity Class of Operation due to having redundant encoders in design.
410-3 | Single PTO tape scale encoder | Provide position feedback to drives | 2 | new environment | Signal failure | 1) Single encoder fail 2) Loss of position feedback | Improper installation or manufacturing defect results in failure | Normal | 1) V&V 2) Redundant encoders | 1) None | 1) Encoder data | Manual switch of encoders onboard Programmatically selected encoders from internal system comparison. | 7 | 1 | 1 | 2 | 4 | Low | Low | Low | Low | [24 empty] | Reduced Severity Class of Operation due to having redundant encoders in design.
410-4 | Single PTO tape scale encoder | Provide position feedback to drives | 2 | new environment | Signal failure | 1) Single encoder fail 2) Loss of position feedback | Software / programming error during program revision. | Normal | 1) V&V 2) Security | 1) None | 1) Encoder data | Manual switch of encoders onboard Manual correction of software/programming error, onboard or remotely. | 5 | 1 | 1 | 6 | 4 | Low | Low | Low | Low | [24 empty] | Reduced Occurrence by 1 level as encoder operation is unlikely to be modified post-deployment and will be fully tested during commissioning and testing.
410-5 | Single PTO tape scale encoder | Provide position feedback to drives | 2 | new environment | Signal failure | 1) Single encoder fail 2) Loss of position feedback | Vibration and/or motion induced failure | Normal | 1) Modal analysis 2) Redundant encoders | 1) None | 1) Encoder data | Manual switch of encoders onboard Programmatically selected encoders from internal system comparison. | 7 | 1 | 1 | 2 | 4 | Low | Low | Low | Low | [24 empty] | Reduced Severity Class of Operation due to having redundant encoders in design.
410-6 | Single PTO tape scale encoder | Provide position feedback to drives | 2 | new environment | Signal failure | 1) Single encoder fail 2) Loss of position feedback | Water induced failure (non-corrosion) | Normal | 1) IP 67 2) Redundant encoders | 1) None | 1) Encoder data | Manual switch of encoders onboard Programmatically selected encoders from internal system comparison. | 7 | 1 | 1 | 2 | 4 | Low | Low | Low | Low | [24 empty] | Reduced Severity Class of Operation due to having redundant encoders in design.
410-7 | Backups + 1 encoders failure | Provide position feedback to drives | 2 | new environment | Encoder failure | 1) Incorrect signal - uncontrolled damping 2) No signal - freewheeling 3) Loss of position feedback | All encoders failed for one PTO | Normal | 1) having installed backups | 1) None | 1) Encoder data | Dry-dock required for repair. | 4 | 1 | 1 | 7 | 7 | Low | Low | Low | Low | [24 empty] | Requires 6 encoders for operation of 3 CU320s. 100% redundant encoders which can be swapped programmatically.
410-8 | Encoder power from M2G | Provide position feedback to drives | 2 | new environment | Signal failure | 1) All encoder fail for one PTO | Power failure to encoder | Normal | 1) Redundant power supplies 2) Powered from M2G | 1) None | 1) Encoder data | manual supply replacement | 3 | 1 | 1 | 6 | 2 | Low | Low | Low | Low | [24 empty] | Power from M2G
410-10 | Generator gap sensor | Provides stator position w.r.t. the outer housing and rotor | 2 | new environment | Signal failure | 1) No gap data from failed sensor | Hardware or wiring failure - corrosion induced - water induced - contamination - vibration | Normal | 1) Redundant sensors on separate stators. | 1) None | 1) Gap sensor data lost | Dry-dock required for repair. Single failure tolerable. | 9 | 1 | 1 | 2 | 2 | Low | Low | Low | Low | [24 empty] | Operation Risk reduced further as loss of sensor data does not affect generator performance. Arranged all failures back to one row as all failures carried the same risk rankings.
410-11 | Torque rod load cell | provides measured stator torque for one stator section | 1 | none | Signal failure | 1) No torque data from failed sensor | Hardware or wiring failure | Normal | 1) Mechanically safe because available torque is limited the load cell's rating, which is well below the mechanical design limit. 2) Redundant sensors on separate stators. | 1) None | 1) Link bar data lost | Dry-dock required for repair. Single failure tolerable. | 8 | 1 | 1 | 3 | 3 | Low | Low | Low | Low | [24 empty] | Mechanically safe because available torque is limited the load cell's rating, which is well below the mechanical design limit.
410-12 | Rail wheel load pin | provides normal force on rail wheels for one stator section | 1 | none | Signal failure | 1) No load data from failed sensor | Hardware or wiring failure | Normal | 1) Redundant sensors | 1) None | 1) Rail wheel load data lost | Dry-dock required for repair. Single failure tolerable | 8 | 1 | 1 | 3 | 3 | Low | Low | Low | Low
410-13 | Seal gap sensor | Provides seal gap position | 2 | new environment | Signal failure | 1) No seal gap data from failed sensor | Hardware or wiring failure | Normal |  | 1) None | 1) Seal gap data lost | Dry-dock required for repair. Single failure tolerable | 9 | 1 | 1 | 2 | 2 | Low | Low | Low | Low | [24 empty] | Operation Risk reduced further as loss of sensor data does not affect generator performance.
410-14 | Main/secondary bearing temperature | Provides bearing temperatures | 2 | Marine application Vibration levels | Signal failure | 1) No bearing temp data | Hardware or wiring failure | Normal | 1) Redundancy 4x per bearing | 1) None | 1) Bearing temp data lost | Dry-dock required for repair. Single failure tolerable | 8 | 1 | 1 | 2 | 1 | Low | Low | Low | Low | [24 empty] | Sensor will be rated for the environment.
410-15 | SCADA enclosure temperature | Provides SCADA enclosure temperatures | 2 | Marine application Vibration levels | Signal failure | 1) No enclosure temperature | Hardware or wiring failure | Normal |  | 1) None | 1) SCADA enclosure data lost | Manual in-situ repair and inspection | 8 | 1 | 1 | 2 | 1 | Low | Low | Low | Low | [24 empty] | Sensor will be rated for the environment.
410-16 | PTO module temperature | Provides PTO structure temperatures | 2 | Marine application Vibration levels | Signal failure | 1) No PTO structure temperature | Hardware or wiring failure | Normal |  | 1) None | 1) PTO structure temp data lost | Manual in-situ repair and inspection | 8 | 1 | 1 | 2 | 1 | Low | Low | Low | Low | [24 empty] | Sensor will be rated for the environment.
410-17 | PTO module humidity | Provides PTO structure humidity | 2 | Marine application Vibration levels | Signal failure | 1) No PTO structure humidity | Hardware or wiring failure | Normal |  | 1) None | 1) PTO structure humidity data lost | Manual in-situ repair and inspection | 8 | 1 | 1 | 2 | 1 | Low | Low | Low | Low | [24 empty] | Sensor will be rated for the environment.
410-18 | Control room temperature | Provides control room temperatures | 2 | Marine application Vibration levels | Signal failure | 1) No control room temperature | Hardware or wiring failure | Normal |  | 1) None | 1) Control room temp data lost | Manual in-situ repair and inspection | 8 | 1 | 1 | 2 | 1 | Low | Low | Low | Low | [24 empty] | Sensor will be rated for the environment.
410-19 | Control room humidity | Provides control room structure humidity | 2 | Marine application Vibration levels | Signal failure | 1) No control room humidity | Hardware or wiring failure | Normal |  | 1) None | 1) Control room humidity data lost | Manual in-situ repair and inspection | 8 | 1 | 1 | 2 | 1 | Low | Low | Low | Low | [24 empty] | Sensor will be rated for the environment.
410-20 | Stator sensor temperatures | Provides sensor temperatures | 2 | Marine application Vibration levels | Signal failure | 1) No sensor temp data from failed sensor | Hardware or wiring failure | Normal |  | 1) None | 1) Sensor temp data lost | Dry-dock required for repair. Single failure tolerable | 8 | 1 | 1 | 2 | 1 | Low | Low | Low | Low | [24 empty] | Sensor will be rated for the environment.
410-21 | Station power draw | Provides station power draw | 2 | Marine application Vibration levels | Signal failure | 1) No station power draw data | Hardware or wiring failure | Normal |  | 1) None | 1) Station power data lost | Manual in-situ repair and inspection | 8 | 1 | 1 | 2 | 2 | Low | Low | Low | Low | [24 empty] | Sensor will be rated for the environment.
410-22 | Bilge water level | Provide bilge water level | 1 | none | Signal failure | 1) No bilge water level data from failed sensor | Hardware or wiring failure | Normal | 1) Redundancy | 1) None | 1) Bilge level data lost | Manual in-situ repair and inspection | 8 | 1 | 1 | 3 | 1 | Low | Low | Low | Low | [24 empty] | Safe (accessible) side of PTO module and redundant sensors rated for the environment.
410-23 | Bilge pump status | Provides bilge pump status data | 1 | none | Signal failure | 1) No bilge pump status | Hardware or wiring failure | Normal | 1) Redundant systems | 1) None | 1) Comparison to float switch data | Manual in-situ repair and inspection | 8 | 1 | 1 | 2 | 1 | Low | Low | Low | Low | [24 empty] | Sensor will be rated for the environment and redundant sensors.
410-24 | Cooling temp, pressure, flow sensor | Provides cooling data | 1 | none | Signal failure | 1) No cooling data from failed sensor | Hardware or wiring failure | Normal |  | 1) None | 1) Cooling parameter data lost | Manual in-situ repair and inspection | 8 | 1 | 1 | 3 | 2 | Low | Low | Low | Low | [24 empty] | Sensor will be rated for the environment and redundant sensors.
410-25 | Fibber optic strain measurement | Provides strain data | 1 | none | Signal failure | 1) No strain data from failed sensor | Hardware or wiring failure | Normal | 1) Redundancy | 1) None | 1) Strain data lost | 1) Interrogator repairable in-situ 2) Single failure tolerable for strain gauge array requires dry dock repair | 8 | 1 | 1 | 3 | 3 | Low | Low | Low | Low | [24 empty] | Sensor will be rated for the environment.
410-26 | Inertial measurement unit (IMU) | Provides nacelle body motion data | 1 | none | Signal failure | 1) No motion data from failed sensor | Hardware or wiring failure | Normal | 1) Redundancy | 1) None | 1) IMU data lost | Manual in-situ repair and inspection | 8 | 1 | 1 | 3 | 3 | Low | Low | Low | Low | [24 empty] | Sensor will be rated for the environment.
410-27 | Communication with M2G | Communicates all M2G data and PTO control commands | 1 | none | Signal failure | 1) No M2G data 2) PTO goes to default control mode in absence of SCADA communication | Hardware or wiring failure | Normal | 1) V&V | 1) None | 1) M2G data lost 2) PTO control not responding | Manual in-situ repair and inspection | 7 | 1 | 1 | 3 | 3 | Low | Low | Low | Low | [24 empty] | PTO goes to default control mode in absence of SCADA communication
410-28 | Real-time AWAC/ADV connection | Provide real-time AWAC data | 1 | none | Signal failure | 1) No AWAC data available | Hardware or wiring failure | Normal | 1) Data can be downloaded later | 1) None | 1) No AWAC data available in real-time | Manual in-situ repair and inspection | 8 | 1 | 1 | 2 | 3 | Low | Low | Low | Low | [24 empty] | Real time data not used in control.
410-29 | Anemometer | Provide wind speed and direction | 1 | none | Signal failure | 1) No WEC wind data | Hardware or wiring failure | Normal | none | 1) None | 1) Wind data lost | Manual in-situ repair and inspection | 9 | 1 | 1 | 2 | 2 | Low | Low | Low | Low | [24 empty] | Sensor will be rated for the environment.
410-30 | GPS & heading sensor | Provide GPS position and heading | 1 | none | Signal failure | 1) No GPS position or heading data from failed sensor | Hardware or wiring failure | Normal | 1) Redundancy | 1) None | 1) GPS & heading data lost | Manual in-situ repair and inspection | 8 | 1 | 1 | 2 | 2 | Low | Low | Low | Low | [24 empty] | Sensor will be rated for the environment.
410-31 | Mooring load cell | Provide mooring load data | 1 | none | Signal failure | 1) No mooring tension from failed sensor | Hardware or wiring failure | Normal | 1) Redundancy 2) Mechanical safety bypass of load cell | 1) Inspection | 1) Mooring data lost | Manual in-situ repair and inspection | 9 | 1 | 1 | 2 | 4 | Low | Low | Low | Med | [24 empty] | Load cells and cabling will be rated for the environment.
410-9 | Power supply | Provide power to SCADA | 1 | none | SCADA offline | 1) No SCADA data 2) PTO goes to defaul control mode 3) Cooling controlers go to default control mode | Power supply failure - corrosion induced - vibration or motion induced - water induced | Normal | 1) Power supply Redundancy 2) Functional redundancy of SCADA components 3) Individual controllers have default modes of operation in absense of SCADA comm. | 1) Status of individual PS | 1) No SCADA | Manual in-situ repair and inspection | 7 | 1 | 1 | 5 | 3 | Low | Low | Med | Low | [24 empty] | Power supply will be rated for the environment. All failure causes fall into the same risk rankings and so kept in one Risk ID.
410-32 | Vibration accelerometer | Provide vibration data | 1 | none | Signal failure | 1) No vibration data from failed sensor | Hardware or wiring failure | Normal | 1) Redundancy | 1) None | 1) Data lost | Manual in-situ repair and inspection on most locations | 8 | 1 | 1 | 3 | 3 | Low | Low | Low | Low | [24 empty] | Sensor will be rated for the environment.
430-1 | PLC | Issue cooling commands | 1 2 | none Marine application Vibration levels | PLC Failure | 1) PTO command failure 2) Cooling system command failure 3) Alarming failure | Corrosion induced failure short circuit | Normal | 1) Marine rated corrosion resistant design 2) Sealed enclosure 3) PTO goes to default control mode in absence of SCADA communication | 1) Visual inspection 2) Fault detection of primary PLC | 1) Primary PLC torque command 2) Primary PLC cooling command | Manual in-situ repair and inspection | 5 | 1 | 1 | 6 | 4 | Low | Low | Low | Low | [24 empty] | Individual controllers have default modes of operation in absense of SCADA comm.
430-2 | PLC | Issue cooling commands | 1 2 | none Marine application Vibration levels | PLC Failure | 1) PTO command failure 2) Cooling system command failure 3) Alarming failure | Improper installation or manufacturing defect results in failure | Normal | 1) V&V (QC) 2) Redundant SCADA controllers 3) PTO goes to default control mode in absence of SCADA communication | 1) Fault detection of primary PLC | 1) Primary PLC torque command 2) Primary PLC cooling command | Manual in-situ repair and inspection | 5 | 1 | 1 | 6 | 4 | Low | Low | Low | Low | [24 empty] | Individual controllers have default modes of operation in absense of SCADA comm.
430-3 | PLC | Issue PTO commands | 1 2 | none Marine application Vibration levels | PLC Failure | 1) PTO command failure 2) Cooling system command failure 3) Alarming failure | Vibration and/or motion induced failure | Normal | 1) Modal analysis 2) Redundant SCADA controllers 3) PTO goes to default control mode in absence of SCADA communication | 1) Fault detection of primary PLC | 1) Primary PLC torque command 2) Primary PLC cooling command | Manual in-situ repair and inspection | 7 | 1 | 1 | 6 | 4 | Low | Low | Med | Low | [24 empty] | Individual controllers have default modes of operation in absense of SCADA comm.
430-4 | PLC | Issue PTO commands | 1 2 | none Marine application Vibration levels | PLC Failure | 1) PTO command failure 2) Cooling system command failure 3) Alarming failure | Water induced failure (non-corrosion) | Normal | 1) Marine rated corrosion resistance design 2) Redundant SCADA controllers 3) PTO goes to default control mode in absence of SCADA communication | 1) Visual inspection 2) Fault detection of primary PLC | 1) Primary PLC torque command 2) Primary PLC cooling command | Manual in-situ repair and inspection | 5 | 1 | 1 | 6 | 4 | Low | Low | Low | Low | [24 empty] | Individual controllers have default modes of operation in absense of SCADA comm.
430-6 | Server PC | Issue cooling commands | 1 2 | none Marine application Vibration levels | PC Failure | 1) Data collection failure 2) HMI visualization failure 3) Alarm reporting failure | Corrosion induced failure short circuit | Normal | 1) Marine rated corrosion resistance design 2) Redundant SCADA controllers | 1) Visual inspection 2) Fault detection of primary SCADA | 1) No primary data collection 2) Primary HMI unavailable | Manual in-situ repair and inspection | 5 | 1 | 1 | 6 | 4 | Low | Low | Low | Low
430-7 | Server PC | Issue cooling commands | 1 2 | none Marine application Vibration levels | PC Failure | 1) Data collection failure 2) HMI visualization failure 3) Alarm reporting failure | Improper installation or manufacturing defect results in failure | Normal | 1) V&V (QC) 2) Redundant SCADA controllers | 1) Fault detection of primary SCADA | 1) No primary data collection 2) Primary HMI unavailable | Manual in-situ repair and inspection | 4 | 1 | 1 | 6 | 4 | Low | Low | Low | Low
430-8 | Server PC | Issue PTO commands | 1 2 | none Marine application Vibration levels | PC Failure | 1) Data collection failure 2) HMI visualization failure 3) Alarm reporting failure | Vibration and/or motion induced failure | Normal | 1) Modal analysis 2) Redundant SCADA controllers 3) Simotion prevents over torque execution 4)Default linear control command issued by Simotion controller | 1) Fault detection of primary SCADA | 1) No primary data collection 2) Primary HMI unavailable | Manual in-situ repair and inspection | 7 | 1 | 1 | 6 | 4 | Low | Low | Med | Low
430-9 | Server PC | Issue PTO commands | 1 2 | none Marine application Vibration levels | PC Failure | 1) Data collection failure 2) HMI visualization failure 3) Alarm reporting failure | Water induced failure (non-corrosion) | Normal | 1) Marine rated corrosion resistance design 2) Redundant SCADA controllers 3) Simotion prevents over torque execution 4) Default torque command issued by Simotion controller | 1) Visual inspection 2) Fault detection of primary SCADA | 1) No primary data collection 2) Primary HMI unavailable | Manual in-situ repair and inspection | 5 | 1 | 1 | 6 | 4 | Low | Low | Low | Low
435-1 | Cooling Command (generate and issue) | Issue cooling commands | 1 | None | Over, under or no cooling command | 1) Under cooling results in PTO shutdown 2) Overcooling wasted energy | Communication issue | Normal | 1) V&V (QC) 2) Redundant SCADA controllers | 1) Fault detection of primary SCADA | 1) Primary SCADA cooling command 2) Stator temperature(s) out of range | Manual in-situ repair and inspection | 6 | 1 | 1 | 5 | 4 | Low | Low | Low | Low | [24 empty] | Cooling commands may be replaced by M2G
435-2 | Cooling Command (generate and issue) | Issue cooling commands | 1 | None | Over, under or no cooling command | 1) Under cooling results in PTO shutdown 2) Overcooling wasted energy | Software / programming error | Normal | 1) V&V (QC) 2) Redundant SCADA controllers | None | 1) Manual check on commissioning 2) Primary SCADA cooling command 3) Stator temperature(s) out of range | Remote programming repair | 6 | 1 | 1 | 5 | 4 | Low | Low | Low | Low
435-3 | PTO Command | Issue PTO commands | 1 | None | SCADA torque command excessive or uncontrolled | 1) High/erratic torque on PTO 2) WEC pitch effected 3) Generator performance affected 4) Potential motoring losses 5) Deviation from control plan | Communication issue | Normal | 1) V&V (QC) 2) Redundant SCADA controllers 3) Simotion prevents over torque execution 4) Default linear control command issued by Simotion controller | 1) Fault detection of primary SCADA | 1) Primary SCADA torque command | Manual in-situ repair and inspection | 6 | 1 | 1 | 5 | 4 | Low | Low | Low | Low | [24 empty] | limited to default linear damping These change with control mode. i.e. linear is limited to 2 quadrant. Simotion is always responsible for machine limits. Cooling is defaulted to max
435-4 | PTO Command | Issue PTO commands | 1 | None | SCADA torque command excessive or uncontrolled | 1) High/erratic torque on PTO 2) WEC pitch effected 3) Generator performance affected 4) Potential motoring losses 5) Deviation from control plan | Software / programming error | Normal | 1) Simotion controller fail safe design 2) Control taken by alternate side PLC | 1) None | 1) Torque command 2) Simotion current output 3) Simotion torque output 4) Stator load cell output | Remote programming repair | 6 | 1 | 1 | 5 | 4 | Low | Low | Low | Low
435-5 | PTO Command | Issue PTO commands | 1 | None | SCADA torque command not issued | 1) Simotion controller takes over torque command 2) Deviation from control plan | Communication issue | Normal | 1) V&V (QC) 2) Redundant SCADA controllers 3) Default linear control command issued by Simotion controller | 1) Fault detection of primary SCADA | 1) Primary SCADA torque command | Manual in-situ repair and inspection | 6 | 1 | 1 | 5 | 4 | Low | Low | Low | Low
435-6 | PTO Command | Issue PTO commands | 1 | None | SCADA torque command not issued | 1) Simotion controller takes over torque command 2) Deviation from control plan | Software / programming error | Normal | 1) V&V (QC) 2) Redundant SCADA controllers 3) Default torque command issued by Simotion controller | 1) Fault detection of primary SCADA | 1) Manual check on commissioning 2) Primary SCADA torque command | Remote programming repair | 6 | 1 | 1 | 5 | 4 | Low | Low | Low | Low

## version history
Title | StingRAY SCADA FMECA
Doc No | SR-0400-RR
Version | 3.5
Authored | E Amon
CPwr Review | A Schacher, P Lenee-Bluhm, J Prudell, E Hammagren, Z Zhang, M Ondusko
Expert Review
Eng man Appr
Corp Appr
Version | Date | Summary
1.0 | 2014-02-03 | Released to GH for review
1.1 | 2014-03-18 | Edits following GH review
2.0 | 2014-11-26 | New format and risk ranking, additional input
3.0 | 2016-07-25 | Updated risk matrix, updated for WEC v3.3 technology
3.5 | 2017-03-03 | Reviewed for 7347, no change to risk ranking
The following contains PROTECTED DATA of Columbia Power Technologies, Inc. not for distribution.

## set up
| Risk = Occ + Sev | [11 empty] | Note:
| Severity | [11 empty] | - 'set up' and 'linkedPage' are both linked to workbook 'FMECA Master v3.xlsx'
Occ | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  |  | - changes to the tables, risk scores, etc must be made in 'FMECA Master v3.xlsx'
10 | Low | Med | Med | Med | Med | High | High | High | High | High
9 | Low | Low | Med | Med | Med | Med | High | High | High | High | low <= | 11
8 | Low | Low | Low | Med | Med | Med | Med | High | High | High | high> | 15
7 | Low | Low | Low | Low | Med | Med | Med | Med | High | High
6 | Low | Low | Low | Low | Low | Med | Med | Med | Med | High
5 | Low | Low | Low | Low | Low | Low | Med | Med | Med | Med
4 | Low | Low | Low | Low | Low | Low | Low | Med | Med | Med |  | Low | Tolerable, no engineer action required
3 | Low | Low | Low | Low | Low | Low | Low | Low | Med | Med |  | Med | Undesirable, consider engineer actions to mitigate risk
2 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Med |  | High | Intolerable, engineering action required
1 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Low
Occurrence | [5 empty] | Severity
Rating | Occurrence |  | Annual Failure Rate | Return Period [years] |  | Rating | Severity | Human Safety |  | Environment |  | WEC Operation |  | Assets
1 | Exceptionally unlikely to occur |  | 1e-05 | 100000 |  | 1 | Insignificant | Negligible injury, effect on health (e.g. band aid) |  | Negligible pollution or no effect on environment |  | Negligible effect on performance |  | Negligible
2 |  |  | 3.1623e-05 | 31600 |  | 2 | [7 empty] | [1.5k USD]
3 | Extremely unlikely to occur |  | 0.0001 | 10000 |  | 3 | Minor | Minor injuries, health effects (e.g. stitches) |  | Minor pollution / slight effect on environment (min disruption on marine life) |  | Minor system degradation |  | Repairable in-situ, at next maintenance interval [5k USD]
4 |  |  | 0.00031623 | 3160 |  | 4 |  | Moderate injuries and/or health effects (e.g. broken bone) |  |  |  | Moderate system degradation (e.g. loss of MoMo) |  | Repairable in-situ, outside maintenance interval (1 day) [15k USD]
5 | Very unlikely to occur |  | 0.001 | 1000 |  | 5 | Major |  |  | Limited levels of pollution, manageable / moderate effect on environment |  |  |  | Repairable in-situ, outside maintenance interval (1 week) [50k USD]
6 |  |  | 0.0031623 | 316 |  | 6 | [5 empty] | Major system degradation or loss of operation for 1 month |  | [150k USD]
7 | Rarely expected to occur |  | 0.01 | 100 |  | 7 | Critical | Hospitalization (with full recovery) |  | Moderate pollution (some clean-up costs) / Serious effect on environment |  | Major system degradation or loss of operation for 3 months |  | Dry dock required for repair [500k USD]
8 |  |  | 0.031623 | 31.6 |  | 8 | [5 empty] | Critical system degradation or loss of operation for 6 months |  | [1.5M USD]
9 | One or more during 20 yr lifetime |  | 0.1 | 10 |  | 9 | Catastrophic | Hospitalization (with lasting disabilities) |  | Major pollution (significant clean-up costs) / disastrous effects on the environment |  | Failure to generate power for remainder of project, complete failure |  | Loss of device [5M USD]
10 |  |  | 0.31623 | 3.16 |  | 10 |  | A fatality

## linkedPage
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | Risk = Occ + Sev | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Note:
0 | 0 | Severity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - 'set up' and 'linkedPage' are both linked to workbook 'FMECA Master v3.xlsx'
0 | Occ | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 0 | 0 | 0 | 0 | 0 | - changes to the tables, risk scores, etc must be made in 'FMECA Master v3.xlsx'
0 | 10 | Low | Med | Med | Med | Med | High | High | High | High | High | 0 | 0 | 0 | 0 | 0
0 | 9 | Low | Low | Med | Med | Med | Med | High | High | High | High | low <= | 11 | 0 | 0 | 0
0 | 8 | Low | Low | Low | Med | Med | Med | Med | High | High | High | high> | 15 | 0 | 0 | 0
0 | 7 | Low | Low | Low | Low | Med | Med | Med | Med | High | High | 0 | 0 | 0 | 0 | 0
0 | 6 | Low | Low | Low | Low | Low | Med | Med | Med | Med | High | 0 | 0 | 0 | 0 | 0
0 | 5 | Low | Low | Low | Low | Low | Low | Med | Med | Med | Med | 0 | 0 | 0 | 0 | 0
0 | 4 | Low | Low | Low | Low | Low | Low | Low | Med | Med | Med | 0 | Low | Tolerable, no engineer action required | 0 | 0
0 | 3 | Low | Low | Low | Low | Low | Low | Low | Low | Med | Med | 0 | Med | Undesirable, consider engineer actions to mitigate risk | 0 | 0
0 | 2 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Med | 0 | High | Intolerable, engineering action required | 0 | 0
0 | 1 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Low | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Occurrence | 0 | 0 | 0 | 0 | 0 | Severity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Rating | Occurrence | 0 | Annual Failure Rate | Return Period [years] | 0 | Rating | Severity | Human Safety | 0 | Environment | 0 | WEC Operation | 0 | Assets | 0
0 | 1 | Exceptionally unlikely to occur | 0 | 1e-05 | 100000 | 0 | 1 | Insignificant | Negligible injury, effect on health (e.g. band aid) | 0 | Negligible pollution or no effect on environment | 0 | Negligible effect on performance | 0 | Negligible | 0
0 | 2 | 0 | 0 | 3.1623e-05 | 31600 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [1.5k USD] | 0
0 | 3 | Extremely unlikely to occur | 0 | 0.0001 | 10000 | 0 | 3 | Minor | Minor injuries, health effects (e.g. stitches) | 0 | Minor pollution / slight effect on environment (min disruption on marine life) | 0 | Minor system degradation | 0 | Repairable in-situ, at next maintenance interval [5k USD] | 0
0 | 4 | 0 | 0 | 0.00031623 | 3160 | 0 | 4 | 0 | Moderate injuries and/or health effects (e.g. broken bone) | 0 | 0 | 0 | Moderate system degradation (e.g. loss of MoMo) | 0 | Repairable in-situ, outside maintenance interval (1 day) [15k USD] | 0
0 | 5 | Very unlikely to occur | 0 | 0.001 | 1000 | 0 | 5 | Major | 0 | 0 | Limited levels of pollution, manageable / moderate effect on environment | 0 | 0 | 0 | Repairable in-situ, outside maintenance interval (1 week) [50k USD] | 0
0 | 6 | 0 | 0 | 0.0031623 | 316 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | Major system degradation or loss of operation for 1 month | 0 | [150k USD] | 0
0 | 7 | Rarely expected to occur | 0 | 0.01 | 100 | 0 | 7 | Critical | Hospitalization (with full recovery) | 0 | Moderate pollution (some clean-up costs) / Serious effect on environment | 0 | Major system degradation or loss of operation for 3 months | 0 | Dry dock required for repair [500k USD] | 0
0 | 8 | 0 | 0 | 0.031623 | 31.6 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | Critical system degradation or loss of operation for 6 months | 0 | [1.5M USD] | 0
0 | 9 | One or more during 20 yr lifetime | 0 | 0.1 | 10 | 0 | 9 | Catastrophic | Hospitalization (with lasting disabilities) | 0 | Major pollution (significant clean-up costs) / disastrous effects on the environment | 0 | Failure to generate power for remainder of project, complete failure | 0 | Loss of device [5M USD] | 0
0 | 10 | 0 | 0 | 0.31623 | 3.16 | 0 | 10 | 0 | A fatality | 0 | 0 | 0 | 0 | 0 | 0 | 0