## Data Rights Notice
PROTECTED RIGHTS NOTICE
These protected data were produced under agreement no. DE-EE0007347 with the U.S. Department of Energy and may not be published, disseminated, or disclosed to others outside the Government until five (5) years from the date the data were first produced, unless express written authorization is obtained from the recipient. Upon expiration of the period of protection set forth in this Notice, the Government shall have unlimited rights in this data. This Notice shall be marked on any reproduction of this data, in whole or in part.

## 0520 Safety & Emergency Systems
[13 empty] | Risk Ranking | [11 empty] | Updated Risk Ranking | [11 empty] | 2nd Updated Risk Ranking
0520 Safety & Emergency Systems FMECA Table | [13 empty] | Severity Class |  |  |  | Risk Class | [7 empty] | Severity Class |  |  |  | Risk Class | [7 empty] | Severity Class |  |  |  | Risk Class
Risk ID | Item Description | Function | Tech. Class | Novel Aspects | Failure Mode | Failure Effects (Local, WEC, System) | Failure Cause(s) | Initial Mode of Operation | Risk Reduction Design | Preventative Detection | Post Failure Detection | Post Failure Repair Strategy (automated, manual) | Occurrence | Human Safety | Environment | Operation | Assets | Human Safety | Environment | Operation | Assets | Recommended Actions | Responsible Party | Actions Taken | Occurrence | Human Safety | Environment | Operation | Assets | Human Safety | Environment | Operation | Assets | 2nd Recommended Actions | Responsible Party (2nd) | Actions Taken (2nd) | Occurrence | Human Safety | Environment | Operation | Assets | Human Safety | Environment | Operation | Assets | Status (open or closed) | Notes
0521-1 | Fire Protection - Automatic Fire Suppression | Automatic Fire Suppression System - Carbon dioxide CO2 - put out fires in electrical enclosures | 1 | none | Automatic suppression activated without a fire | 1) Enclosures filled with fire suppression CO2. | 1) Defect in pressurized CO2 line routed through the enclosures | Normal | 1) COTS product 2) V&V (QC) | 1) Visual inspection | 1) SCADA - fire & fire spreading 2) Visual - fire | 1) Repair in-situ repair if possible. 2) dry dock | 4 | 4 | 4 | 7 | 7 | Low | Low | Low | Low
0521-2 | Fire Protection - smoke alarms | Alarms in case of smoke in enclosures & compartments | 1 | none | False alarm | false fire alarm activated. | Sensor defect/contamination | Normal | V&V (QC) | 1) Visual inspection | 1) SCADA - fire & fire spreading 2) Visual - fire | 1) Repair in-situ repair if possible. 2) dry dock | 4 | 2 | 2 | 5 | 5 | Low | Low | Low | Low
0522-1 | Flooding Alarms | Monitor high bilge level sensor and alarm if reached. | 1 | none | No high water alarm | No alarm while bilge pumps running continuously | Faulty wiring/moisture induced failure | Normal | V&V (QC) | 1) Visual inspection | 1) Bilge pump running continuously 2) Surveillance system – visual inspection | 1) Repair in-situ repair if possible. 2) dry dock | 4 | 5 | 4 | 8 | 8 | Low | Low | Med | Med
0533-2 | Evacuation Alarms | Sound and flashing lights in case of fire, flooding, collision, or other operator iniated evacuation alarm. | 1 | none | No alarm/lights in one of compartments: - topside - control room - Both PTOs - Nacelle tube | Personnel not properly warned in case of an emergency | Faulty wiring/moisture induced failure | Normal | V&V (QC) | 1) Visual inspection | 1) Maintenance inspection | 1) Repair in-situ repair if possible. 2) dry dock | 4 | 5 | 2 | 7 | 7 | Low | Low | Low | Low
0524-1 | Air Quality Monitoring | Monitor air quality in all compartments. Report air qaulity to SCADA, initiate alarm if outside of specified levels of O2, CO2, H2O etc. | 1 | none | Loss of air quality monitoring of one of the compartments: - topside - control room - Both PTOs - Nacelle tube | Requires ventilation and manual air quality monitoring for access/egress until sensor is replaced. | Faulty wiring/moisture induced failure | Normal | V&V (QC) | 1) Visual inspection | 1) Emergency system control diagnostics - sensor fault alarm | 1) Repair in-situ repair if possible. 2) dry dock | 4 | 6 | 4 | 7 | 7 | Low | Low | Low | Low
0525-1 | Access Alarms | Monitor hatch acccess sensors and alarm based on SCADA operational setting. Indicate hatch status | 1 | none | Failed OPEN, hatch sensor inducates false open | Hatch indicates open while closed | Faulty wiring/moisture induced failure | Normal | V&V (QC) | 1) Visual inspection | 1) Emergency system control diagnostics - sensor fault alarm | 1) Repair in-situ repair if possible. 2) dry dock | 5 | 4 | 4 | 7 | 7 | Low | Low | Med | Med
0526-1 | Systems - Estop Monitoring | Monitor Estop circuits and alarm if the safety interlocks are broken | 1 | none | E-stop fails OPEN, false e-stop indicated | E-stop alarm without E-stop | Faulty wiring/moisture induced failure | Normal | V&V (QC) | 1) Visual inspection | 1) Emergency system control diagnostics - sensor fault alarm | 1) Repair in-situ repair if possible. 2) dry dock | 4 | 7 | 4 | 7 | 7 | Low | Low | Low | Low
0527-1 | Safety Controller | Safety PLC monitor safety systems and provide control logic for alarms and data interface | 1 | none | Complete safety system monitoring loss | Alarms sound - false with alarm on (Automatic fire supression and bilge pumping still function without indication) | Faulty wiring/moisture induced failure | Normal | V&V (QC) | 1) Visual inspection | 1) SCADA diagnositcs | 1) Repair in-situ repair if possible. 2) dry dock | 4 | 4 | 4 | 7 | 7 | Low | Low | Low | Low
0528-1 | Safety Communications | Communication components between safety PLC and designated fiber-optic line to shore. | 1 | none | Loss of designated communicatoins channel | Commincations alarm, communicatoins switch to SCADA channel back-up | Faulty wiring/moisture induced failure | Normal | V&V (QC) | 1) Visual inspection | 1) Emergency system control diagnostics | 1) Repair in-situ repair if possible. 2) dry dock | 4 | 4 | 4 | 7 | 7 | Low | Low | Low | Low

## version history
Title | StingRAY Safety & Emergency Systems FMECA
Doc No | SR-0520-RR
Version | 3.5
Authored | J Prudell
Reviewed
Approved Dist.
Approved Final
Version | Date | Summary
1.0 | 2013-11-08 | Preliminary, not released
2.0 | 2016-02-01 | Released to RC for review
3.0 | 2016-07-25 | Updated risk matrix, updated for WEC v3.3 technology
3.5 | 2017-02-27 | Reviewed for 7347, no change to risk ranking
The following contains PROTECTED DATA of Columbia Power Technologies, Inc. not for distribution.

## set up
| Risk = Occ + Sev | [11 empty] | Note:
| Severity | [11 empty] | - 'set up' and 'linkedPage' are both linked to workbook 'FMECA Master v3.xlsx'
Occ | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  |  | - changes to the tables, risk scores, etc must be made in 'FMECA Master v3.xlsx'
10 | Low | Med | Med | Med | Med | High | High | High | High | High
9 | Low | Low | Med | Med | Med | Med | High | High | High | High | low <= | 11
8 | Low | Low | Low | Med | Med | Med | Med | High | High | High | high> | 15
7 | Low | Low | Low | Low | Med | Med | Med | Med | High | High
6 | Low | Low | Low | Low | Low | Med | Med | Med | Med | High
5 | Low | Low | Low | Low | Low | Low | Med | Med | Med | Med
4 | Low | Low | Low | Low | Low | Low | Low | Med | Med | Med |  | Low | Tolerable, no engineer action required
3 | Low | Low | Low | Low | Low | Low | Low | Low | Med | Med |  | Med | Undesirable, consider engineer actions to mitigate risk
2 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Med |  | High | Intolerable, engineering action required
1 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Low
Occurrence | [5 empty] | Severity
Rating | Occurrence |  | Annual Failure Rate | Return Period [years] |  | Rating | Severity | Human Safety |  | Environment |  | WEC Operation |  | Assets
1 | Exceptionally unlikely to occur |  | 1e-05 | 100000 |  | 1 | Insignificant | Negligible injury, effect on health (e.g. band aid) |  | Negligible pollution or no effect on environment |  | Negligible effect on performance |  | Negligible
2 |  |  | 3.1623e-05 | 31600 |  | 2 | [7 empty] | [1.5k USD]
3 | Extremely unlikely to occur |  | 0.0001 | 10000 |  | 3 | Minor | Minor injuries, health effects (e.g. stitches) |  | Minor pollution / slight effect on environment (min disruption on marine life) |  | Minor system degradation |  | Repairable in-situ, at next maintenance interval [5k USD]
4 |  |  | 0.00031623 | 3160 |  | 4 |  | Moderate injuries and/or health effects (e.g. broken bone) |  |  |  | Moderate system degradation (e.g. loss of MoMo) |  | Repairable in-situ, outside maintenance interval (1 day) [15k USD]
5 | Very unlikely to occur |  | 0.001 | 1000 |  | 5 | Major |  |  | Limited levels of pollution, manageable / moderate effect on environment |  |  |  | Repairable in-situ, outside maintenance interval (1 week) [50k USD]
6 |  |  | 0.0031623 | 316 |  | 6 | [5 empty] | Major system degradation or loss of operation for 1 month |  | [150k USD]
7 | Rarely expected to occur |  | 0.01 | 100 |  | 7 | Critical | Hospitalization (with full recovery) |  | Moderate pollution (some clean-up costs) / Serious effect on environment |  | Major system degradation or loss of operation for 3 months |  | Dry dock required for repair [500k USD]
8 |  |  | 0.031623 | 31.6 |  | 8 | [5 empty] | Critical system degradation or loss of operation for 6 months |  | [1.5M USD]
9 | One or more during 20 yr lifetime |  | 0.1 | 10 |  | 9 | Catastrophic | Hospitalization (with lasting disabilities) |  | Major pollution (significant clean-up costs) / disastrous effects on the environment |  | Failure to generate power for remainder of project, complete failure |  | Loss of device [5M USD]
10 |  |  | 0.31623 | 3.16 |  | 10 |  | A fatality

## linkedPage
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | Risk = Occ + Sev | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Note:
0 | 0 | Severity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - 'set up' and 'linkedPage' are both linked to workbook 'FMECA Master v3.xlsx'
0 | Occ | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 0 | 0 | 0 | 0 | 0 | - changes to the tables, risk scores, etc must be made in 'FMECA Master v3.xlsx'
0 | 10 | Low | Med | Med | Med | Med | High | High | High | High | High | 0 | 0 | 0 | 0 | 0
0 | 9 | Low | Low | Med | Med | Med | Med | High | High | High | High | low <= | 11 | 0 | 0 | 0
0 | 8 | Low | Low | Low | Med | Med | Med | Med | High | High | High | high> | 15 | 0 | 0 | 0
0 | 7 | Low | Low | Low | Low | Med | Med | Med | Med | High | High | 0 | 0 | 0 | 0 | 0
0 | 6 | Low | Low | Low | Low | Low | Med | Med | Med | Med | High | 0 | 0 | 0 | 0 | 0
0 | 5 | Low | Low | Low | Low | Low | Low | Med | Med | Med | Med | 0 | 0 | 0 | 0 | 0
0 | 4 | Low | Low | Low | Low | Low | Low | Low | Med | Med | Med | 0 | Low | Tolerable, no engineer action required | 0 | 0
0 | 3 | Low | Low | Low | Low | Low | Low | Low | Low | Med | Med | 0 | Med | Undesirable, consider engineer actions to mitigate risk | 0 | 0
0 | 2 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Med | 0 | High | Intolerable, engineering action required | 0 | 0
0 | 1 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Low | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Occurrence | 0 | 0 | 0 | 0 | 0 | Severity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Rating | Occurrence | 0 | Annual Failure Rate | Return Period [years] | 0 | Rating | Severity | Human Safety | 0 | Environment | 0 | WEC Operation | 0 | Assets | 0
0 | 1 | Exceptionally unlikely to occur | 0 | 1e-05 | 100000 | 0 | 1 | Insignificant | Negligible injury, effect on health (e.g. band aid) | 0 | Negligible pollution or no effect on environment | 0 | Negligible effect on performance | 0 | Negligible | 0
0 | 2 | 0 | 0 | 3.1623e-05 | 31600 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [1.5k USD] | 0
0 | 3 | Extremely unlikely to occur | 0 | 0.0001 | 10000 | 0 | 3 | Minor | Minor injuries, health effects (e.g. stitches) | 0 | Minor pollution / slight effect on environment (min disruption on marine life) | 0 | Minor system degradation | 0 | Repairable in-situ, at next maintenance interval [5k USD] | 0
0 | 4 | 0 | 0 | 0.00031623 | 3160 | 0 | 4 | 0 | Moderate injuries and/or health effects (e.g. broken bone) | 0 | 0 | 0 | Moderate system degradation (e.g. loss of MoMo) | 0 | Repairable in-situ, outside maintenance interval (1 day) [15k USD] | 0
0 | 5 | Very unlikely to occur | 0 | 0.001 | 1000 | 0 | 5 | Major | 0 | 0 | Limited levels of pollution, manageable / moderate effect on environment | 0 | 0 | 0 | Repairable in-situ, outside maintenance interval (1 week) [50k USD] | 0
0 | 6 | 0 | 0 | 0.0031623 | 316 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | Major system degradation or loss of operation for 1 month | 0 | [150k USD] | 0
0 | 7 | Rarely expected to occur | 0 | 0.01 | 100 | 0 | 7 | Critical | Hospitalization (with full recovery) | 0 | Moderate pollution (some clean-up costs) / Serious effect on environment | 0 | Major system degradation or loss of operation for 3 months | 0 | Dry dock required for repair [500k USD] | 0
0 | 8 | 0 | 0 | 0.031623 | 31.6 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | Critical system degradation or loss of operation for 6 months | 0 | [1.5M USD] | 0
0 | 9 | One or more during 20 yr lifetime | 0 | 0.1 | 10 | 0 | 9 | Catastrophic | Hospitalization (with lasting disabilities) | 0 | Major pollution (significant clean-up costs) / disastrous effects on the environment | 0 | Failure to generate power for remainder of project, complete failure | 0 | Loss of device [5M USD] | 0
0 | 10 | 0 | 0 | 0.31623 | 3.16 | 0 | 10 | 0 | A fatality | 0 | 0 | 0 | 0 | 0 | 0 | 0