## Data Rights Notice
PROTECTED RIGHTS NOTICE
These protected data were produced under agreement no. DE-EE0007347 with the U.S. Department of Energy and may not be published, disseminated, or disclosed to others outside the Government until five (5) years from the date the data were first produced, unless express written authorization is obtained from the recipient. Upon expiration of the period of protection set forth in this Notice, the Government shall have unlimited rights in this data. This Notice shall be marked on any reproduction of this data, in whole or in part.

## 0560 Cooling System
[13 empty] | Risk Ranking | [11 empty] | Updated Risk Ranking | [11 empty] | 2nd Updated Risk Ranking
00560 Cooling System FMECA Table | [13 empty] | Severity Class |  |  |  | Risk Class | [7 empty] | Severity Class |  |  |  | Risk Class | [7 empty] | Severity Class |  |  |  | Risk Class
Risk ID | Item Description | Function | Tech. Class | Novel Aspects | Failure Mode | Failure Effects (Local, WEC, System) | Failure Cause(s) | Initial Mode of Operation | Risk Reduction Design | Preventative Detection | Post Failure Detection | Post Failure Repair Strategy (automated, manual) | Occurrence | Human Safety | Environment | Operation | Assets | Human Safety | Environment | Operation | Assets | Recommended Actions | Responsible Party | Actions Taken | Occurrence | Human Safety | Environment | Operation | Assets | Human Safety | Environment | Operation | Assets | 2nd Recommended Actions | Responsible Party (2nd) | Actions Taken (2nd) | Occurrence | Human Safety | Environment | Operation | Assets | Human Safety | Environment | Operation | Assets | Status (open or closed) | Notes
0560-1 | Cooling Pipes | Contain coolant loop | 1 | none | Large coolant leak | 1) Loss of PTO 2) Loss of AC power generation 3) bilge pumps run | Improper installation or manufacturing defect results in failure | Normal | 1) V&V (QC) | Moisture sensors Inspections | SCADA Diagnostics Bilge pumping | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | PEX tubing, marine design, etc.
0561/0562 - 1 | Cooling pumps | Provide electric power to cooling pumps | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Corrosion induced failure short circuit | Normal | 1)Marine rated corrosion resistance designed enclosure 2) Redundant design, two cooling pumps per PTO | 1) Visual inspection | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Check the QC procedures on all component manufacturing.
0561/0562 - 2 | Cooling pumps | Provide electric power to cooling pumps | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Improper installation or manufacturing defect results in failure | Normal | 1) V&V (QC) | none | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Vibration isolation design for all electric components
0561/0562 - 3 | Cooling pumps | Provide electric power to cooling pumps | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Water induced failure (non-corrosion) | Normal | 1)Marine rated waterproof enclosure 2) Redundant design, two cooling pumps per PTO | 1) SCADA diagnostics 2) Visual inspection | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Corrosion prevention design for all components
0561/0562 - 4 | Cooling pumps | Provide electric power to cooling pumps | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Vibration and/or motion induced failure | Normal | 1) Vibration analysis 2) Equipment and installation designed for dynamic environment 3) Redundant design, two cooling pumps per PTO | none | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Waterproofing all components
0561/0562 - 5 | Cooling pumps | Provide electric power to cooling pumps | 1 | none | Electrical Failure - smoke/fire | 1) Loss of PTO 2) Loss of AC power generation | All of the faults 1 thru 4 | Normal | 1) Vibration analysis 2) Equipment and installation designed for dynamic environment 3) Redundant design, two cooling pumps per PTO | none | 1) Smoke alarms - reduce time to electrically isolate 2) Over-current protection - for electrical isolation 3) Automatic fire suppression 4)SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 7 | 7 | Low | Low | Med | Med | Waterproofing all components
0563/0564 - 1 | Cooling pump controllers | Pump water to Stbd/Port PTO stator segments | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Corrosion induced failure short circuit | Normal | 1)Marine rated corrosion resistance designed enclosure 2) Redundant design, two cooling pumps per PTO | 1) Visual inspection | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Check the QC procedures on all component manufacturing.
0563/0564 - 2 | Cooling pump controllers | Pump water to Stbd/Port PTO stator segments | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Improper installation or manufacturing defect results in failure | Normal | 1) V&V (QC) | none | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Vibration isolation design for all electric components
0563/0564 - 3 | Cooling pump controllers | Pump water to Stbd/Port PTO stator segments | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Water induced failure (non-corrosion) | Normal | 1)Marine rated waterproof enclosure 2) Redundant design, two cooling pumps per PTO | 1) SCADA diagnostics 2) Visual inspection | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Corrosion prevention design for all components
0563/0564 - 4 | Cooling pump controllers | Pump water to Stbd/Port PTO stator segments | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Vibration and/or motion induced failure | Normal | 1) Vibration analysis 2) Equipment and installation designed for dynamic environment 3) Redundant design, two cooling pumps per PTO | none | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Waterproofing all components
0563/0564 - 5 | Cooling pump controllers | Pump water to Stbd/Port PTO stator segments | 1 | none | Electrical Failure - smoke/fire | 1) Loss of PTO 2) Loss of AC power generation | All of the faults 1 thru 4 | Normal | 1) Vibration analysis 2) Equipment and installation designed for dynamic environment 3) Redundant design, two cooling pumps per PTO | none | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 5 | 1 | 7 | 7 | Low | Low | Med | Med | Waterproofing all components
0565 | Hull Heat Exchanger | Exchange cooling water heat with ocean water | 1 | none | Leak | 1) Flooding 2) Loss of cooling 3) Loss of PTO | Vibration and/or motion induced failure | Normal | 1) Marine design/rated heat exchanger 2) V&V (QC) | none | SCADA Diagnostics Bilge sensors | Manual in-situ inspection and repair | 6 | 5 | 1 | 6 | 5 | Low | Low | Med | Low | Look into boi-fouling in warm climates - bio-fouling prevention
0567- 1 | Control room Cooling pump | Provide electric power to cooling pumps | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Corrosion induced failure short circuit | Normal | 1)Marine rated corrosion resistance designed enclosure 2) Redundant design, two cooling pumps per PTO | 1) Visual inspection | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Check the QC procedures on all component manufacturing.
0567- 2 | Control room Cooling pump | Provide electric power to cooling pumps | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Improper installation or manufacturing defect results in failure | Normal | 1) V&V (QC) | none | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Vibration isolation design for all electric components
0567- 3 | Control room Cooling pump | Provide electric power to cooling pumps | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Water induced failure (non-corrosion) | Normal | 1)Marine rated waterproof enclosure 2) Redundant design, two cooling pumps per PTO | 1) SCADA diagnostics 2) Visual inspection | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Corrosion prevention design for all components
0567- 4 | Control room Cooling pump | Provide electric power to cooling pumps | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Vibration and/or motion induced failure | Normal | 1) Vibration analysis 2) Equipment and installation designed for dynamic environment 3) Redundant design, two cooling pumps per PTO | none | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Waterproofing all components
0567- 5 | Control room Cooling pump | Provide electric power to cooling pumps | 1 | none | Electrical Failure - smoke/fire | 1) Loss of PTO 2) Loss of AC power generation | All of the faults 1 thru 4 | Normal | 1) Vibration analysis 2) Equipment and installation designed for dynamic environment 3) Redundant design, two cooling pumps per PTO | none | 1) Smoke alarms - reduce time to electrically isolate 2) Over-current protection - for electrical isolation 3) Automatic fire suppression 4)SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 5 | 1 | 7 | 7 | Low | Low | Med | Med | Waterproofing all components
0568- 1 | Cooling pump | Pump water to Stbd/Port PTO stator segments | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Corrosion induced failure short circuit | Normal | 1)Marine rated corrosion resistance designed enclosure 2) Redundant design, two cooling pumps per PTO | 1) Visual inspection | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Check the QC procedures on all component manufacturing.
0568- 2 | Cooling pump | Pump water to Stbd/Port PTO stator segments | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Improper installation or manufacturing defect results in failure | Normal | 1) V&V (QC) | none | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Vibration isolation design for all electric components
0568- 3 | Cooling pump | Pump water to Stbd/Port PTO stator segments | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Water induced failure (non-corrosion) | Normal | 1)Marine rated waterproof enclosure 2) Redundant design, two cooling pumps per PTO | 1) SCADA diagnostics 2) Visual inspection | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Corrosion prevention design for all components
0568- 4 | Cooling pump | Pump water to Stbd/Port PTO stator segments | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Vibration and/or motion induced failure | Normal | 1) Vibration analysis 2) Equipment and installation designed for dynamic environment 3) Redundant design, two cooling pumps per PTO | none | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Waterproofing all components
0568- 5 | Cooling pump | Pump water to Stbd/Port PTO stator segments | 1 | none | Electrical Failure - smoke/fire | 1) Loss of PTO 2) Loss of AC power generation | All of the faults 1 thru 4 | Normal | 1) Vibration analysis 2) Equipment and installation designed for dynamic environment 3) Redundant design, two cooling pumps per PTO | none | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 5 | 1 | 7 | 7 | Low | Low | Med | Med | Waterproofing all components

## version history
Title | StingRAY Cooling System FMECA
Doc No | SR-0560-RR
Version | 3.5
Authored | J Prudell
Reviewed
Approved Dist.
Approved Final
Version | Date | Summary
1.0 | 2013-11-06 | Preliminary, not released
1.1 | 2014-01-28 | Preliminary, not released
2.0 | 2015-02-01 | released to RC for review
3.0 | 2016-07-25 | Updated risk matrix, updated for WEC v3.3 technology
3.5 | 2017-02-27 | Reviewed for 7347, no change to risk ranking
The following contains PROTECTED DATA of Columbia Power Technologies, Inc. not for distribution.

## set up
| Risk = Occ + Sev | [11 empty] | Note:
| Severity | [11 empty] | - 'set up' and 'linkedPage' are both linked to workbook 'FMECA Master v3.xlsx'
Occ | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  |  | - changes to the tables, risk scores, etc must be made in 'FMECA Master v3.xlsx'
10 | Low | Med | Med | Med | Med | High | High | High | High | High
9 | Low | Low | Med | Med | Med | Med | High | High | High | High | low <= | 11
8 | Low | Low | Low | Med | Med | Med | Med | High | High | High | high> | 15
7 | Low | Low | Low | Low | Med | Med | Med | Med | High | High
6 | Low | Low | Low | Low | Low | Med | Med | Med | Med | High
5 | Low | Low | Low | Low | Low | Low | Med | Med | Med | Med
4 | Low | Low | Low | Low | Low | Low | Low | Med | Med | Med |  | Low | Tolerable, no engineer action required
3 | Low | Low | Low | Low | Low | Low | Low | Low | Med | Med |  | Med | Undesirable, consider engineer actions to mitigate risk
2 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Med |  | High | Intolerable, engineering action required
1 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Low
Occurrence | [5 empty] | Severity
Rating | Occurrence |  | Annual Failure Rate | Return Period [years] |  | Rating | Severity | Human Safety |  | Environment |  | WEC Operation |  | Assets
1 | Exceptionally unlikely to occur |  | 1e-05 | 100000 |  | 1 | Insignificant | Negligible injury, effect on health (e.g. band aid) |  | Negligible pollution or no effect on environment |  | Negligible effect on performance |  | Negligible
2 |  |  | 3.1623e-05 | 31600 |  | 2 | [7 empty] | [1.5k USD]
3 | Extremely unlikely to occur |  | 0.0001 | 10000 |  | 3 | Minor | Minor injuries, health effects (e.g. stitches) |  | Minor pollution / slight effect on environment (min disruption on marine life) |  | Minor system degradation |  | Repairable in-situ, at next maintenance interval [5k USD]
4 |  |  | 0.00031623 | 3160 |  | 4 |  | Moderate injuries and/or health effects (e.g. broken bone) |  |  |  | Moderate system degradation (e.g. loss of MoMo) |  | Repairable in-situ, outside maintenance interval (1 day) [15k USD]
5 | Very unlikely to occur |  | 0.001 | 1000 |  | 5 | Major |  |  | Limited levels of pollution, manageable / moderate effect on environment |  |  |  | Repairable in-situ, outside maintenance interval (1 week) [50k USD]
6 |  |  | 0.0031623 | 316 |  | 6 | [5 empty] | Major system degradation or loss of operation for 1 month |  | [150k USD]
7 | Rarely expected to occur |  | 0.01 | 100 |  | 7 | Critical | Hospitalization (with full recovery) |  | Moderate pollution (some clean-up costs) / Serious effect on environment |  | Major system degradation or loss of operation for 3 months |  | Dry dock required for repair [500k USD]
8 |  |  | 0.031623 | 31.6 |  | 8 | [5 empty] | Critical system degradation or loss of operation for 6 months |  | [1.5M USD]
9 | One or more during 20 yr lifetime |  | 0.1 | 10 |  | 9 | Catastrophic | Hospitalization (with lasting disabilities) |  | Major pollution (significant clean-up costs) / disastrous effects on the environment |  | Failure to generate power for remainder of project, complete failure |  | Loss of device [5M USD]
10 |  |  | 0.31623 | 3.16 |  | 10 |  | A fatality

## linkedPage
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | Risk = Occ + Sev | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Note:
0 | 0 | Severity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - 'set up' and 'linkedPage' are both linked to workbook 'FMECA Master v3.xlsx'
0 | Occ | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 0 | 0 | 0 | 0 | 0 | - changes to the tables, risk scores, etc must be made in 'FMECA Master v3.xlsx'
0 | 10 | Low | Med | Med | Med | Med | High | High | High | High | High | 0 | 0 | 0 | 0 | 0
0 | 9 | Low | Low | Med | Med | Med | Med | High | High | High | High | low <= | 11 | 0 | 0 | 0
0 | 8 | Low | Low | Low | Med | Med | Med | Med | High | High | High | high> | 15 | 0 | 0 | 0
0 | 7 | Low | Low | Low | Low | Med | Med | Med | Med | High | High | 0 | 0 | 0 | 0 | 0
0 | 6 | Low | Low | Low | Low | Low | Med | Med | Med | Med | High | 0 | 0 | 0 | 0 | 0
0 | 5 | Low | Low | Low | Low | Low | Low | Med | Med | Med | Med | 0 | 0 | 0 | 0 | 0
0 | 4 | Low | Low | Low | Low | Low | Low | Low | Med | Med | Med | 0 | Low | Tolerable, no engineer action required | 0 | 0
0 | 3 | Low | Low | Low | Low | Low | Low | Low | Low | Med | Med | 0 | Med | Undesirable, consider engineer actions to mitigate risk | 0 | 0
0 | 2 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Med | 0 | High | Intolerable, engineering action required | 0 | 0
0 | 1 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Low | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Occurrence | 0 | 0 | 0 | 0 | 0 | Severity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Rating | Occurrence | 0 | Annual Failure Rate | Return Period [years] | 0 | Rating | Severity | Human Safety | 0 | Environment | 0 | WEC Operation | 0 | Assets | 0
0 | 1 | Exceptionally unlikely to occur | 0 | 1e-05 | 100000 | 0 | 1 | Insignificant | Negligible injury, effect on health (e.g. band aid) | 0 | Negligible pollution or no effect on environment | 0 | Negligible effect on performance | 0 | Negligible | 0
0 | 2 | 0 | 0 | 3.1623e-05 | 31600 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [1.5k USD] | 0
0 | 3 | Extremely unlikely to occur | 0 | 0.0001 | 10000 | 0 | 3 | Minor | Minor injuries, health effects (e.g. stitches) | 0 | Minor pollution / slight effect on environment (min disruption on marine life) | 0 | Minor system degradation | 0 | Repairable in-situ, at next maintenance interval [5k USD] | 0
0 | 4 | 0 | 0 | 0.00031623 | 3160 | 0 | 4 | 0 | Moderate injuries and/or health effects (e.g. broken bone) | 0 | 0 | 0 | Moderate system degradation (e.g. loss of MoMo) | 0 | Repairable in-situ, outside maintenance interval (1 day) [15k USD] | 0
0 | 5 | Very unlikely to occur | 0 | 0.001 | 1000 | 0 | 5 | Major | 0 | 0 | Limited levels of pollution, manageable / moderate effect on environment | 0 | 0 | 0 | Repairable in-situ, outside maintenance interval (1 week) [50k USD] | 0
0 | 6 | 0 | 0 | 0.0031623 | 316 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | Major system degradation or loss of operation for 1 month | 0 | [150k USD] | 0
0 | 7 | Rarely expected to occur | 0 | 0.01 | 100 | 0 | 7 | Critical | Hospitalization (with full recovery) | 0 | Moderate pollution (some clean-up costs) / Serious effect on environment | 0 | Major system degradation or loss of operation for 3 months | 0 | Dry dock required for repair [500k USD] | 0
0 | 8 | 0 | 0 | 0.031623 | 31.6 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | Critical system degradation or loss of operation for 6 months | 0 | [1.5M USD] | 0
0 | 9 | One or more during 20 yr lifetime | 0 | 0.1 | 10 | 0 | 9 | Catastrophic | Hospitalization (with lasting disabilities) | 0 | Major pollution (significant clean-up costs) / disastrous effects on the environment | 0 | Failure to generate power for remainder of project, complete failure | 0 | Loss of device [5M USD] | 0
0 | 10 | 0 | 0 | 0.31623 | 3.16 | 0 | 10 | 0 | A fatality | 0 | 0 | 0 | 0 | 0 | 0 | 0