## Data Rights Notice
PROTECTED RIGHTS NOTICE
These protected data were produced under agreement no. DE-EE0007347 with the U.S. Department of Energy and may not be published, disseminated, or disclosed to others outside the Government until five (5) years from the date the data were first produced, unless express written authorization is obtained from the recipient. Upon expiration of the period of protection set forth in this Notice, the Government shall have unlimited rights in this data. This Notice shall be marked on any reproduction of this data, in whole or in part.

## 0520 Safety & Emergency Systems
[13 empty] | Risk Ranking | [11 empty] | Updated Risk Ranking | [11 empty] | 2nd Updated Risk Ranking
0520 Safety & Emergency Systems FMECA Table | [13 empty] | Severity Class |  |  |  | Risk Class | [7 empty] | Severity Class |  |  |  | Risk Class | [7 empty] | Severity Class |  |  |  | Risk Class
Risk ID | Item Description | Function | Tech. Class | Novel Aspects | Failure Mode | Failure Effects (Local, WEC, System) | Failure Cause(s) | Initial Mode of Operation | Risk Reduction Design | Preventative Detection | Post Failure Detection | Post Failure Repair Strategy (automated, manual) | Occurrence | Human Safety | Environment | Operation | Assets | Human Safety | Environment | Operation | Assets | Recommended Actions | Responsible Party | Actions Taken | Occurrence | Human Safety | Environment | Operation | Assets | Human Safety | Environment | Operation | Assets | 2nd Recommended Actions | Responsible Party (2nd) | Actions Taken (2nd) | Occurrence | Human Safety | Environment | Operation | Assets | Human Safety | Environment | Operation | Assets | Status (open or closed) | Notes
0521-1 | Fire Protection - Automatic Fire Suppression | Automatic Fire Suppression System - Carbon dioxide CO2 - put out fires in electrical enclosures | 2 | Maintenance intervals; Humidity temperature; Vibrations | Automatic suppression activated without a fire (while occupied) | 1) Enclosures filled with fire suppression CO2. | 1) Defect in pressurized CO2 line routed through the enclosures 2) Sensor failure | Normal | 1) COTS product 2) V&V (QC) | 1) Visual inspection | 1) SCADA - fire & fire spreading 2) Visual - fire | 1) Repair in-situ repair if possible. 2) dry dock | 5 | 10 | 4 | 4 | 4 | Med | Low | Low | Low | 1. Locked out CO2 valve procedure required upon entry 2. No pressurization unless system is deployed 3. Pressure monitoring of system to detect if there is a leak. 4. Design to minimise piping and number of connection points and where possible avoid flexible tubing. 5. C02 leak could cause a low oxygen environment and risk of fatality. Procedures to be in place for confined space entry. 6. Carry personal gas/oxygen detectors (Risk assess before entry) | [24 empty] | Failure leading to leak is detectable prior to fire therefore severity class can be reduced for operation and assets. Occurrence class could be lower Manufacturing documentation demonstrating reliability of the component needs to be compatible with the occurrence class assigned to all components in the safety and emergency system
0521-2 | Fire Protection - Automatic Fire Suppression | Automatic Fire Suppression System - Carbon dioxide CO2 - put out fires in electrical enclosures | 2 | Maintenance intervals; Humidity temperature; Vibrations | Fire suppression fails to activate | Electrical fire is not contained | 1) Sensor Failure 2) CO2 delivery system blocked/valve failure on demand | Normal |  |  |  | 1) Repair in-situ if possible. 2) dry dock | 5 | 4 | 4 | 7 | 7 | Low | Low | Med | Med | 1.Probability of failure on demand of system can be reduced by regular inspection/testing of equipment. 2. Fire resistant components and cables for critical systems if required for achieving 'safe state' during a fire.
0521-3 | Fire Protection - smoke alarms | Alarms in case of smoke in enclosures & compartments | 2 | Maintenance intervals; Humidity temperature; Vibrations | False alarm | false fire alarm activated. | Sensor defect/contamination | Normal | V&V (QC) | 1) Visual inspection 2) Periodic testing (monthly?) | 1) SCADA - fire & fire spreading 2) Visual - fire | 1) Repair in-situ if possible. 2) dry dock | 7 | 2 | 2 | 4 | 4 | Low | Low | Low | Low | [25 empty] | For spurious alarms assume low risk, only requiring a repair to the faulty system.
0521-4 | Fire Protection - smoke alarms | Alarms in case of smoke in enclosures & compartments | 2 | Maintenance intervals; Humidity temperature; Vibrations | Alarm fails to activate | NO alarm | Sensor defect Alarm power failure | Normal |  | 1. Regular inspection and testing | 1. If manned, human senses (evacuate premise or use alternative fire supression system) |  | 6 | 7 | 4 | 4 | 4 | Med | Low | Low | Low | 1. Regular testing of alarm, and sensor to confirm function. 2. Redundant sensors to ensure safety of persons on board. 3. Design to ensure easy escape routes in case of emergency meeting SOLAS requirements. 4. Prior to boarding, train personnel in proper fire identification/supression/evacuation | [24 empty] | If manned, personnel onboard should be able to detect fire quickly and respond by evacuation or other means to ensure minor burn injuries and no fatalities. Severity includes only replacement of sensor for operation and assets
0522-1 | Flooding Alarms | Monitor high bilge level sensor and alarm if reached. | 2 | Maintenance intervals; Humidity temperature; Vibrations | No high water alarm | No alarm while bilge pumps running continuously | Faulty wiring/moisture induced failure | Normal | V&V (QC) | 1) Visual inspection 2) Regular inspection and testing | 1) Water detected in hull | 1) Repair in-situ repair if possible. 2) dry dock | 7 | 8 | 4 | 4 | 4 | Med | Low | Low | Low | 1. Regular testing of alarm, and sensor to confirm function. 2. Redundant sensors/multiple means of flood detection (bilge running etc.) 3. Design to ensure easy escape routes in case of emergency meeting SOLAS requirements. 4. Prior to boarding, train personnel in proper vessel evacuation (ideally to nearby support vessel) | [24 empty] | Severity considers evacuation-trained personnel onboard and support vessel for human safety but only replacement of sensor for operation and assets
0533-2 | Evacuation Alarms | Sound and flashing lights in case of fire, flooding, collision, or other operator iniated evacuation alarm. | 2 | Maintenance intervals; Humidity temperature; Vibrations | No alarm/lights in one of compartments: - topside - control room - PTO - Nacelle tube | Personnel not properly warned in case of an emergency | Faulty wiring/moisture induced failure | Normal | V&V (QC) | 1) Visual inspection | 1) Maintenance inspection | 1) Repair in-situ repair if possible. 2) dry dock | 7 | 8 | 2 | 4 | 4 | Med | Low | Low | Low | 1. Regular testing of alarm and sensor to confirm function. 2. Multiple alarms - battery UPS backup. 3. Design to ensure easy escape routes in case of emergency meeting SOLAS requirements. 4. Emergency equipment onboard, if manned and no support vessel | [24 empty] | Severity considers evacuation-trained personnel onboard and support vessel for human safety but only replacement of sensor for operation and assets
0524-1 | Air Quality Monitoring | Monitor air quality in all compartments. Report air qaulity to SCADA, initiate alarm if outside of specified levels of O2, CO2, H2O etc. | 2 | Maintenance intervals; Humidity temperature; Vibrations | Loss of air quality monitoring of one of the compartments: - topside - control room - Both PTOs - Nacelle tube | Requires ventilation and manual air quality monitoring for access/egress until sensor is replaced. | Faulty wiring/moisture induced failure | Normal | V&V (QC) | 1) Visual inspection | 1) Emergency system control diagnostics - sensor fault alarm | 1) Repair in-situ repair if possible. 2) dry dock | 5 | 10 | 4 | 4 | 4 | Med | Low | Low | Low | 1. Regular testing of alarm, and sensor to confirm function. 2.Carry personal gas/oxygen detectors (Risk assess before entry) 3. Confined space entry procedures to be in place. 4. Locked out CO2 valve procedure required upon entry | [24 empty] | Severity considers the loss of life for Human Safety but only replacement of alarm for operation and assets
0525-1 | Access Alarms | Monitor hatch acccess sensors and alarm based on SCADA operational setting. Indicate hatch status | 1 | none | Failed OPEN, hatch sensor inducates false open | Hatch indicates open while closed | Faulty wiring/moisture induced failure | Normal | V&V (QC) | 1) Visual inspection | 1) Emergency system control diagnostics - sensor fault alarm | 1) Repair in-situ repair if possible. 2) dry dock | 6 | 1 | 1 | 3 | 3 | Low | Low | Low | Low | [25 empty] | Low risk as only consequence is an additional maintenance visit to check hatch status. Add redundant sensors for confirmation of sensor operation, reducing occurrence level to 6. HS&E severity classes lowered to 1, a false open is low risk but requires inspection. O&A severity classes lowered to 3 accordingly.
0525-2 | Access Alarms | Monitor hatch access sensors and alarm based on SCADA operational setting. Indicate hatch status | 1 | none | Alarm fails to activate to signal open hatch | Hatch indicates closed while open | Faulty wiring/moisture induced failure | Normal |  | 1) Visual inspection of sensor to check for damage | 1) Emergency system control diagnostics - sensor fault alarm | Repair in situ | 5 | 1 | 4 | 7 | 7 | Low | Low | Med | Med | [25 empty] | Open hatch could allow water ingress damage to electrical equipment and possibly impacting stability. Visual check is primary method of ensuring closure. Add redundant sensors for confirmation of sensor operation, reducing occurrence level to 5. HS severity class reduced to 1 as a false closed is low risk to personnel (access is open while onboard) but is a risk to equipment.
0526-1 | Systems - Estop Monitoring | Monitor Estop circuits and alarm if the safety interlocks are broken | 2 | Maintenance intervals; Humidity temperature; Vibrations | E-stop fails OPEN, false e-stop indicated | E-stop alarm without E-stop | Faulty wiring/moisture induced failure | Normal | V&V (QC) | 1) Visual inspection | 1) Emergency system control diagnostics - sensor fault alarm | 1) Repair in-situ repair if possible. 2) dry dock | 4 | 7 | 4 | 7 | 7 | Low | Low | Low | Low | [25 empty] | Replacement of e-stop system only - low consequence of failure
0526-2 | Systems - Estop Monitoring | Monitor Estop circuits and alarm if the safety interlocks are broken | 2 | Maintenance intervals; Humidity temperature; Vibrations | E-stop fails on demand | Safety barrier of E-stop is compromised. | Faulty wiring/moisture induced failure | Normal |  | Regular testing |  | 1) Repair in-situ repair if possible. 2) dry dock | 6 | 9 | 4 | 7 | 7 | Med | Low | Med | Med | 1) Use of high reliability components for safety system 2) Regular testing to ensure functionality | [24 empty] | Failure of emergency stop on demand would have significant consequences including potential human safety.
0527-1 | Safety Controller | Safety PLC monitor safety systems and provide control logic for alarms and data interface | 2 | Maintenance intervals; Humidity temperature; Vibrations | Complete safety system monitoring loss | Alarms sound - false with alarm on (Automatic fire supression and bilge pumping still function without indication) | Faulty wiring/moisture induced failure | Normal | V&V (QC) | 1) Visual inspection | 1) SCADA diagnositcs | 1) Repair in-situ repair if possible. 2) dry dock | 4 | 4 | 4 | 7 | 7 | Low | Low | Low | Low | [25 empty] | See comment in ID 0521-1 on technology class and novelty and general comment
0527-2 | Safety Controller | Safety PLC monitor safety systems and provide control logic for alarms and data interface | 2 | Maintenance intervals; Humidity temperature; Vibrations | Complete safety system monitoring loss | Fails to signal action when trip levels reached | Faulty wiring or control logic error | Normal |  | 1)Testing of control logic during commissioning 2) Regular inspection and testing of safety systems | 1) SCADA diagnositcs | 1) Repair in-situ repair if possible. 2) dry dock | 7 | 8 | 4 | 7 | 7 | Med | Low | Med | Med | 1) Approved test procedures to be witnessed during commissioning 2) Back-up battery 3) Regular testing and maintenance on system 4) Train personnel to monitor their environment during maintenance or while onboard | [24 empty] | Redundancy of alarm systems helps decrease risk. If manned, evacuation equipment supplied and personnel trained to monitor their environment while onboard
0528-1 | Safety Communications | Communication components between safety PLC and designated fiber-optic line to shore. | 2 | Maintenance intervals; Humidity temperature; Vibrations | Loss of designated communicatoins channel | Communications alarm, communicatoins switch to SCADA channel back-up | Faulty wiring/moisture induced failure | Normal | V&V (QC) | 1) Visual inspection | 1) Emergency system control diagnostics | 1) Repair in-situ repair if possible. 2) dry dock | 4 | 4 | 4 | 7 | 7 | Low | Low | Low | Low
650-1 | Emergency lighting | Lighting in case of emergency power loss | 1 | none | fails to function in emergency | No lighting in an emergency evacuation | power supply fails to charge UPS, | Normal |  | Regular testing |  | Replace faulty systems in situ | 7 | 4 | 4 | 4 | 4 | Low | Low | Low | Low | 1. Flashlights available on board 2. multiple UPS powered lights 3. Solar cells and energy storage 4. Back-up battery | [24 empty] | Human safety unlikely to be impacted by darkness alone; switch to portable lights and back-up battery and/or evacuate the vessel

## version history
Title | StingRAY Safety & Emergency Systems FMECA
Doc No | SR-0520-RR
Version | 3.7
Authored | J. Prudell
Reviewed | K. Rhiefrank, A. McKee
Approved Dist.
Approved Final
Version | Date | Summary
1.0 | 2013-11-08 | Preliminary, not released
2.0 | 2016-02-01 | Released to RC for review
3.0 | 2016-07-25 | Updated risk matrix, updated for WEC v3.3 technology (no change for safety)… incorporate RC comments
3.6 | 2018-06-05 | updated for 7347 WBS 14 BP2 (updates from RC comments not in BP1 RR)
3.6 | 2018-06-22 | K. Rhinefrank--Reviewed - Unaccreptaable risks to personnel -- Design change is required to remove gas risk and must include a LOTO solution that keeps pressurized CO2 external to occupied spaces.
3.7 | 2018-06-22 | A. McKee reviewed red flags
The following contains PROTECTED DATA of Columbia Power Technologies, Inc. not for distribution.

## set up
| Risk = Occ + Sev | [11 empty] | Note:
| Severity | [11 empty] | - 'set up' and 'linkedPage' are both linked to workbook 'FMECA Master v3.xlsx'
Occ | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  |  | - changes to the tables, risk scores, etc must be made in 'FMECA Master v3.xlsx'
10 | Low | Med | Med | Med | Med | High | High | High | High | High
9 | Low | Low | Med | Med | Med | Med | High | High | High | High | low <= | 11
8 | Low | Low | Low | Med | Med | Med | Med | High | High | High | high> | 15
7 | Low | Low | Low | Low | Med | Med | Med | Med | High | High
6 | Low | Low | Low | Low | Low | Med | Med | Med | Med | High
5 | Low | Low | Low | Low | Low | Low | Med | Med | Med | Med
4 | Low | Low | Low | Low | Low | Low | Low | Med | Med | Med |  | Low | Tolerable, no engineer action required
3 | Low | Low | Low | Low | Low | Low | Low | Low | Med | Med |  | Med | Undesirable, consider engineer actions to mitigate risk
2 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Med |  | High | Intolerable, engineering action required
1 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Low
Occurrence | [5 empty] | Severity
Rating | Occurrence |  | Annual Failure Rate | Return Period [years] |  | Rating | Severity | Human Safety |  | Environment |  | WEC Operation |  | Assets
1 | Exceptionally unlikely to occur |  | 1e-05 | 100000 |  | 1 | Insignificant | Negligible injury, effect on health (e.g. band aid) |  | Negligible pollution or no effect on environment |  | Negligible effect on performance |  | Negligible
2 |  |  | 3.1623e-05 | 31600 |  | 2 | [7 empty] | [1.5k USD]
3 | Extremely unlikely to occur |  | 0.0001 | 10000 |  | 3 | Minor | Minor injuries, health effects (e.g. stitches) |  | Minor pollution / slight effect on environment (min disruption on marine life) |  | Minor system degradation |  | Repairable in-situ, at next maintenance interval [5k USD]
4 |  |  | 0.00031623 | 3160 |  | 4 |  | Moderate injuries and/or health effects (e.g. broken bone) |  |  |  | Moderate system degradation (e.g. loss of MoMo) |  | Repairable in-situ, outside maintenance interval (1 day) [15k USD]
5 | Very unlikely to occur |  | 0.001 | 1000 |  | 5 | Major |  |  | Limited levels of pollution, manageable / moderate effect on environment |  |  |  | Repairable in-situ, outside maintenance interval (1 week) [50k USD]
6 |  |  | 0.0031623 | 316 |  | 6 | [5 empty] | Major system degradation or loss of operation for 1 month |  | [150k USD]
7 | Rarely expected to occur |  | 0.01 | 100 |  | 7 | Critical | Hospitalization (with full recovery) |  | Moderate pollution (some clean-up costs) / Serious effect on environment |  | Major system degradation or loss of operation for 3 months |  | Dry dock required for repair [500k USD]
8 |  |  | 0.031623 | 31.6 |  | 8 | [5 empty] | Critical system degradation or loss of operation for 6 months |  | [1.5M USD]
9 | One or more during 20 yr lifetime |  | 0.1 | 10 |  | 9 | Catastrophic | Hospitalization (with lasting disabilities) |  | Major pollution (significant clean-up costs) / disastrous effects on the environment |  | Failure to generate power for remainder of project, complete failure |  | Loss of device [5M USD]
10 |  |  | 0.31623 | 3.16 |  | 10 |  | A fatality

## linkedPage
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | Risk = Occ + Sev | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Note:
0 | 0 | Severity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - 'set up' and 'linkedPage' are both linked to workbook 'FMECA Master v3.xlsx'
0 | Occ | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 0 | 0 | 0 | 0 | 0 | - changes to the tables, risk scores, etc must be made in 'FMECA Master v3.xlsx'
0 | 10 | Low | Med | Med | Med | Med | High | High | High | High | High | 0 | 0 | 0 | 0 | 0
0 | 9 | Low | Low | Med | Med | Med | Med | High | High | High | High | low <= | 11 | 0 | 0 | 0
0 | 8 | Low | Low | Low | Med | Med | Med | Med | High | High | High | high> | 15 | 0 | 0 | 0
0 | 7 | Low | Low | Low | Low | Med | Med | Med | Med | High | High | 0 | 0 | 0 | 0 | 0
0 | 6 | Low | Low | Low | Low | Low | Med | Med | Med | Med | High | 0 | 0 | 0 | 0 | 0
0 | 5 | Low | Low | Low | Low | Low | Low | Med | Med | Med | Med | 0 | 0 | 0 | 0 | 0
0 | 4 | Low | Low | Low | Low | Low | Low | Low | Med | Med | Med | 0 | Low | Tolerable, no engineer action required | 0 | 0
0 | 3 | Low | Low | Low | Low | Low | Low | Low | Low | Med | Med | 0 | Med | Undesirable, consider engineer actions to mitigate risk | 0 | 0
0 | 2 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Med | 0 | High | Intolerable, engineering action required | 0 | 0
0 | 1 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Low | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Occurrence | 0 | 0 | 0 | 0 | 0 | Severity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Rating | Occurrence | 0 | Annual Failure Rate | Return Period [years] | 0 | Rating | Severity | Human Safety | 0 | Environment | 0 | WEC Operation | 0 | Assets | 0
0 | 1 | Exceptionally unlikely to occur | 0 | 1e-05 | 100000 | 0 | 1 | Insignificant | Negligible injury, effect on health (e.g. band aid) | 0 | Negligible pollution or no effect on environment | 0 | Negligible effect on performance | 0 | Negligible | 0
0 | 2 | 0 | 0 | 3.1623e-05 | 31600 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [1.5k USD] | 0
0 | 3 | Extremely unlikely to occur | 0 | 0.0001 | 10000 | 0 | 3 | Minor | Minor injuries, health effects (e.g. stitches) | 0 | Minor pollution / slight effect on environment (min disruption on marine life) | 0 | Minor system degradation | 0 | Repairable in-situ, at next maintenance interval [5k USD] | 0
0 | 4 | 0 | 0 | 0.00031623 | 3160 | 0 | 4 | 0 | Moderate injuries and/or health effects (e.g. broken bone) | 0 | 0 | 0 | Moderate system degradation (e.g. loss of MoMo) | 0 | Repairable in-situ, outside maintenance interval (1 day) [15k USD] | 0
0 | 5 | Very unlikely to occur | 0 | 0.001 | 1000 | 0 | 5 | Major | 0 | 0 | Limited levels of pollution, manageable / moderate effect on environment | 0 | 0 | 0 | Repairable in-situ, outside maintenance interval (1 week) [50k USD] | 0
0 | 6 | 0 | 0 | 0.0031623 | 316 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | Major system degradation or loss of operation for 1 month | 0 | [150k USD] | 0
0 | 7 | Rarely expected to occur | 0 | 0.01 | 100 | 0 | 7 | Critical | Hospitalization (with full recovery) | 0 | Moderate pollution (some clean-up costs) / Serious effect on environment | 0 | Major system degradation or loss of operation for 3 months | 0 | Dry dock required for repair [500k USD] | 0
0 | 8 | 0 | 0 | 0.031623 | 31.6 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | Critical system degradation or loss of operation for 6 months | 0 | [1.5M USD] | 0
0 | 9 | One or more during 20 yr lifetime | 0 | 0.1 | 10 | 0 | 9 | Catastrophic | Hospitalization (with lasting disabilities) | 0 | Major pollution (significant clean-up costs) / disastrous effects on the environment | 0 | Failure to generate power for remainder of project, complete failure | 0 | Loss of device [5M USD] | 0
0 | 10 | 0 | 0 | 0.31623 | 3.16 | 0 | 10 | 0 | A fatality | 0 | 0 | 0 | 0 | 0 | 0 | 0