## Data Rights Notice
PROTECTED RIGHTS NOTICE
These protected data were produced under agreement no. DE-EE0007347 with the U.S. Department of Energy and may not be published, disseminated, or disclosed to others outside the Government until five (5) years from the date the data were first produced, unless express written authorization is obtained from the recipient. Upon expiration of the period of protection set forth in this Notice, the Government shall have unlimited rights in this data. This Notice shall be marked on any reproduction of this data, in whole or in part.

## 0560 Cooling System
[13 empty] | Risk Ranking | [11 empty] | Updated Risk Ranking | [11 empty] | 2nd Updated Risk Ranking
00560 Cooling System FMECA Table | [13 empty] | Severity Class |  |  |  | Risk Class | [7 empty] | Severity Class |  |  |  | Risk Class | [7 empty] | Severity Class |  |  |  | Risk Class
Risk ID | Item Description | Function | Tech. Class | Novel Aspects | Failure Mode | Failure Effects (Local, WEC, System) | Failure Cause(s) | Initial Mode of Operation | Risk Reduction Design | Preventative Detection | Post Failure Detection | Post Failure Repair Strategy (automated, manual) | Occurrence | Human Safety | Environment | Operation | Assets | Human Safety | Environment | Operation | Assets | Recommended Actions | Responsible Party | Actions Taken | Occurrence | Human Safety | Environment | Operation | Assets | Human Safety | Environment | Operation | Assets | 2nd Recommended Actions | Responsible Party (2nd) | Actions Taken (2nd) | Occurrence | Human Safety | Environment | Operation | Assets | Human Safety | Environment | Operation | Assets | Status (open or closed) | Notes
0560-1 | Cooling Pipes | Contain coolant loop | 1 | none | Large coolant leak | 1) Loss of PTO 2) Loss of AC power generation 3) bilge pumps run | Improper installation or manufacturing defect results in failure | Normal | 1) V&V (QC) | Moisture sensors Inspections | SCADA Diagnostics Bilge pumping | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | PEX tubing, marine design, etc. 1.Piping connections are frequent causes of leakage and should be minimised in the design and be accessible for inspection/repair. 2.Pressure test system during commissioning for strength/leaks. 3. Flexible tubing is prone to wear and should be avoided where possible or have suitable protection.
0560-2 | Cooling Pipes | Contain coolant loop | 1 | none | Blockage | 1) Loss of one PTO 2) Reduction in power production | Contamination of cooling circuit | Normal | Filters in cooling circuit. Flush system during commissioning and prevent contamination during installation | Pressure/temperature sensors in cooling circuit | Temperature rise in PTO |  | 4 | 1 | 1 | 6 | 5 | Low | Low | Low | Low | [25 empty] | Low risk so no additional actions but please note: Occurrence assumed to be low due to short deployment period but should be monitored to develop knowledge of risk. Blockage due to build up of contaminants can be detected by pressure changes in cooling circuit over time. To be monitored during in service life and used coolant inspected during maintenance changes for signs of contamination.
0561 - 1 | Cooling pumps | Pump water to PTO stator segments | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Corrosion induced failure short circuit | Normal | 1)Marine rated corrosion resistance designed enclosure 2) Redundant design, two cooling pumps per PTO | 1) Visual inspection | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | 1. For selected severity class cooling pumps are to be repaired/replaced in-situ, to be confirmed in design. 2. PTO will be shutdown to prevent overheating and consequential damage when its cooling pump fails. 3. Documented evidence from manufacturer to demonstrate pump is suitable for marine environment and failure rate of pumps is within CP reliability targets.
0561 - 2 | Cooling pumps | Pump water to PTO stator segments | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Improper installation or manufacturing defect results in failure | Normal | 1) V&V (QC) | none | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | 1. Documented evidence from manufacturer to demonstrate pump is suitable for marine environment and failure rate of pumps is within StingRAY reliability targets. 2. Inspection and commissioning to be performed on installed system according to approved commissioning procedures.
0561 - 3 | Cooling pumps | Pump water to PTO stator segments | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Water induced failure (non-corrosion) | Normal | 1)Marine rated waterproof enclosure 2) Redundant design, two cooling pumps per PTO | 1) SCADA diagnostics 2) Visual inspection | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | 1. Documented evidence from manufacturer of ingress protection rating suitable for environment.
0561 - 4 | Cooling pumps | Pump water to PTO stator segments | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Vibration and/or motion induced failure | Normal | 1) Vibration analysis 2) Equipment and installation designed for dynamic environment 3) Redundant design, two cooling pumps per PTO | none | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | 1.Documented evidence from manufacturer to demonstrate failure rate is within the acceptance criteria for the expected level of vibration in WEC. 2. Vibration level to be monitored after deployment to confirm vibration levels
0561 - 5 | Cooling pumps | Pump water to PTO stator segments | 1 | none | Electrical Failure - smoke/fire | 1) Loss of PTO 2) Loss of AC power generation | All of the faults 1 thru 4 | Normal | 1) Vibration analysis 2) Equipment and installation designed for dynamic environment 3) Redundant design, two cooling pumps per PTO | none | 1) Smoke alarms - reduce time to electrically isolate 2) Over-current protection - for electrical isolation 3) Automatic fire suppression 4)SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 7 | 7 | Low | Low | Med | Med | 1. Fire detection and suppression systems for electrical fires.
0562 - 1 | Cooling pump controllers | Provide electric power to / control cooling pumps | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Corrosion induced failure short circuit | Normal | 1)Marine rated corrosion resistance designed enclosure 2) Redundant design, two cooling pumps per PTO | 1) Visual inspection | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Recommended action the same as risk ID 0561-1
562 - 2 | Cooling pump controllers | Provide electric power to / control cooling pumps | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Improper installation or manufacturing defect results in failure | Normal | 1) V&V (QC) | none | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Recommended action the same as risk ID 0561-2
562 - 3 | Cooling pump controllers | Provide electric power to / control cooling pumps | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Water induced failure (non-corrosion) | Normal | 1)Marine rated waterproof enclosure 2) Redundant design, two cooling pumps per PTO | 1) SCADA diagnostics 2) Visual inspection | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Recommended action the same as risk ID 0561-3
562 - 4 | Cooling pump controllers | Provide electric power to / control cooling pumps | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Vibration and/or motion induced failure | Normal | 1) Vibration analysis 2) Equipment and installation designed for dynamic environment 3) Redundant design, two cooling pumps per PTO | none | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Recommended action the same as risk ID 0561-4
562 - 5 | Cooling pump controllers | Provide electric power to / control cooling pumps | 1 | none | Electrical Failure - smoke/fire | 1) Loss of PTO 2) Loss of AC power generation | All of the faults 1 thru 4 | Normal | 1) Vibration analysis 2) Equipment and installation designed for dynamic environment 3) Redundant design, two cooling pumps per PTO | none | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 5 | 1 | 7 | 7 | Low | Low | Med | Med | Recommended action the same as risk ID 0561-5
0563-1 | Hull Heat Exchanger | Exchange cooling water heat with ocean water | 1 | none | Leak | 1) Flooding 2) Loss of cooling 3) Loss of PTO | Vibration and/or motion induced failure | Normal | 1) Marine design/rated heat exchanger 2) V&V (QC) | none | SCADA Diagnostics Bilge sensors | Manual in-situ inspection and repair | 6 | 5 | 1 | 6 | 5 | Low | Low | Med | Low | The recommended action is to investigate the dynamic movement of the rotor and assess the effect of the vibration loads on the structure integrity (fatigue) of the component. The acceptance criteria for the maximum vibration level shall be defined. The FE analysis, considering these failure mechanisms, need to demonstrate the structural strength is within the acceptance criteria in the standard and the impact on functionality of the device is within the acceptance criteria. The monitoring of the vibration shall be done to identify the level of vibrations during in-service life. If any excessive vibration is detected, intervention is required to reduce the vibration level below the maximum level, as defined in the acceptance criteria (conditioning monitoring).
0563-2 | Hull Heat Exchanger | Exchange cooling water heat with ocean water | 1 | none | Leak | 1) Flooding 2) Loss of cooling 3) Loss of PTO | Biofouling | Normal | 1) Marine design/rated heat exchanger 2) V&V (QC) | none | SCADA Diagnostics Bilge sensors | Manual in-situ inspection and repair | 6 | 5 | 1 | 6 | 5 | Low | Low | Med | Low | 1. For selected severity class heat exchanger is to be repaired/replaced in-situ, to be confirmed in design. 2. Documented evidence from manufacturer to demonstrate heat exchanger is suitable for marine environment and used in similar conditions. 3. Reduction in efficiency due to biofouling to be taken into account during design.
0564- 1 | Control room Cooling pump | Pump cooling water to electric plant, climate control, and aux systems | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Corrosion induced failure short circuit | Normal | 1)Marine rated corrosion resistance designed enclosure 2) Redundant design, two cooling pumps per PTO | 1) Visual inspection | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Recommended action the same as risk ID 0561-1
0564- 2 | Control room Cooling pump | Pump cooling water to electric plant, climate control, and aux systems | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Improper installation or manufacturing defect results in failure | Normal | 1) V&V (QC) | none | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Recommended action the same as risk ID 0561-2
0564- 3 | Control room Cooling pump | Pump cooling water to electric plant, climate control, and aux systems | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Water induced failure (non-corrosion) | Normal | 1)Marine rated waterproof enclosure 2) Redundant design, two cooling pumps per PTO | 1) SCADA diagnostics 2) Visual inspection | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Recommended action the same as risk ID 0561-3
0564- 4 | Control room Cooling pump | Pump cooling water to electric plant, climate control, and aux systems | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Vibration and/or motion induced failure | Normal | 1) Vibration analysis 2) Equipment and installation designed for dynamic environment 3) Redundant design, two cooling pumps per PTO | none | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Recommended action the same as risk ID 0561-4
0564- 5 | Control room Cooling pump | Pump cooling water to electric plant, climate control, and aux systems | 1 | none | Electrical Failure - smoke/fire | 1) Loss of PTO 2) Loss of AC power generation | All of the faults 1 thru 4 | Normal | 1) Vibration analysis 2) Equipment and installation designed for dynamic environment 3) Redundant design, two cooling pumps per PTO | none | 1) Smoke alarms - reduce time to electrically isolate 2) Over-current protection - for electrical isolation 3) Automatic fire suppression 4)SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 5 | 1 | 7 | 7 | Low | Low | Med | Med | Recommended action the same as risk ID 0561-5
0565- 1 | Control room Cooling pump Controllers | Pump water to Stbd/Port PTO stator segments | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Corrosion induced failure short circuit | Normal | 1)Marine rated corrosion resistance designed enclosure 2) Redundant design, two cooling pumps per PTO | 1) Visual inspection | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Recommended action the same as risk ID 0561-1
0565- 2 | Control room Cooling pump Controllers | Pump water to Stbd/Port PTO stator segments | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Improper installation or manufacturing defect results in failure | Normal | 1) V&V (QC) | none | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Recommended action the same as risk ID 0561-2
0565- 3 | Control room Cooling pump Controllers | Pump water to Stbd/Port PTO stator segments | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Water induced failure (non-corrosion) | Normal | 1)Marine rated waterproof enclosure 2) Redundant design, two cooling pumps per PTO | 1) SCADA diagnostics 2) Visual inspection | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Recommended action the same as risk ID 0561-3
0565- 4 | Control room Cooling pump Controllers | Pump water to Stbd/Port PTO stator segments | 1 | none | Electrical Failure | 1) Loss of PTO 2) Loss of AC power generation | Vibration and/or motion induced failure | Normal | 1) Vibration analysis 2) Equipment and installation designed for dynamic environment 3) Redundant design, two cooling pumps per PTO | none | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 1 | 1 | 6 | 5 | Low | Low | Med | Low | Recommended action the same as risk ID 0561-4
0565- 5 | Control room Cooling pump Controllers | Pump water to Stbd/Port PTO stator segments | 1 | none | Electrical Failure - smoke/fire | 1) Loss of PTO 2) Loss of AC power generation | All of the faults 1 thru 4 | Normal | 1) Vibration analysis 2) Equipment and installation designed for dynamic environment 3) Redundant design, two cooling pumps per PTO | none | SCADA Diagnostics | Manual in-situ inspection and repair | 6 | 5 | 1 | 7 | 7 | Low | Low | Med | Med | Recommended action the same as risk ID 0561-5

## version history
Title | StingRAY Cooling System FMECA
Doc No | SR-0560-RR
Version | 3.6
Authored | J Prudell
Reviewed
Approved Dist.
Approved Final
Version | Date | Summary
1.0 | 2013-11-06 | Preliminary, not released
1.1 | 2014-01-28 | Preliminary, not released
2.0 | 2015-02-01 | released to RC for review
3.0 | 2016-07-25 | Updated risk matrix, updated for WEC v3.3 technology (limited changes for cooling system)… incorporate RC comments
3.6 | 2018-06-05 | updated for 7347 WBS 14 BP2 (updates from RC comments not in BP1 RR)
The following contains PROTECTED DATA of Columbia Power Technologies, Inc. not for distribution.

## set up
| Risk = Occ + Sev | [11 empty] | Note:
| Severity | [11 empty] | - 'set up' and 'linkedPage' are both linked to workbook 'FMECA Master v3.xlsx'
Occ | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  |  | - changes to the tables, risk scores, etc must be made in 'FMECA Master v3.xlsx'
10 | Low | Med | Med | Med | Med | High | High | High | High | High
9 | Low | Low | Med | Med | Med | Med | High | High | High | High | low <= | 11
8 | Low | Low | Low | Med | Med | Med | Med | High | High | High | high> | 15
7 | Low | Low | Low | Low | Med | Med | Med | Med | High | High
6 | Low | Low | Low | Low | Low | Med | Med | Med | Med | High
5 | Low | Low | Low | Low | Low | Low | Med | Med | Med | Med
4 | Low | Low | Low | Low | Low | Low | Low | Med | Med | Med |  | Low | Tolerable, no engineer action required
3 | Low | Low | Low | Low | Low | Low | Low | Low | Med | Med |  | Med | Undesirable, consider engineer actions to mitigate risk
2 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Med |  | High | Intolerable, engineering action required
1 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Low
Occurrence | [5 empty] | Severity
Rating | Occurrence |  | Annual Failure Rate | Return Period [years] |  | Rating | Severity | Human Safety |  | Environment |  | WEC Operation |  | Assets
1 | Exceptionally unlikely to occur |  | 1e-05 | 100000 |  | 1 | Insignificant | Negligible injury, effect on health (e.g. band aid) |  | Negligible pollution or no effect on environment |  | Negligible effect on performance |  | Negligible
2 |  |  | 3.1623e-05 | 31600 |  | 2 | [7 empty] | [1.5k USD]
3 | Extremely unlikely to occur |  | 0.0001 | 10000 |  | 3 | Minor | Minor injuries, health effects (e.g. stitches) |  | Minor pollution / slight effect on environment (min disruption on marine life) |  | Minor system degradation |  | Repairable in-situ, at next maintenance interval [5k USD]
4 |  |  | 0.00031623 | 3160 |  | 4 |  | Moderate injuries and/or health effects (e.g. broken bone) |  |  |  | Moderate system degradation (e.g. loss of MoMo) |  | Repairable in-situ, outside maintenance interval (1 day) [15k USD]
5 | Very unlikely to occur |  | 0.001 | 1000 |  | 5 | Major |  |  | Limited levels of pollution, manageable / moderate effect on environment |  |  |  | Repairable in-situ, outside maintenance interval (1 week) [50k USD]
6 |  |  | 0.0031623 | 316 |  | 6 | [5 empty] | Major system degradation or loss of operation for 1 month |  | [150k USD]
7 | Rarely expected to occur |  | 0.01 | 100 |  | 7 | Critical | Hospitalization (with full recovery) |  | Moderate pollution (some clean-up costs) / Serious effect on environment |  | Major system degradation or loss of operation for 3 months |  | Dry dock required for repair [500k USD]
8 |  |  | 0.031623 | 31.6 |  | 8 | [5 empty] | Critical system degradation or loss of operation for 6 months |  | [1.5M USD]
9 | One or more during 20 yr lifetime |  | 0.1 | 10 |  | 9 | Catastrophic | Hospitalization (with lasting disabilities) |  | Major pollution (significant clean-up costs) / disastrous effects on the environment |  | Failure to generate power for remainder of project, complete failure |  | Loss of device [5M USD]
10 |  |  | 0.31623 | 3.16 |  | 10 |  | A fatality

## linkedPage
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | Risk = Occ + Sev | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Note:
0 | 0 | Severity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - 'set up' and 'linkedPage' are both linked to workbook 'FMECA Master v3.xlsx'
0 | Occ | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 0 | 0 | 0 | 0 | 0 | - changes to the tables, risk scores, etc must be made in 'FMECA Master v3.xlsx'
0 | 10 | Low | Med | Med | Med | Med | High | High | High | High | High | 0 | 0 | 0 | 0 | 0
0 | 9 | Low | Low | Med | Med | Med | Med | High | High | High | High | low <= | 11 | 0 | 0 | 0
0 | 8 | Low | Low | Low | Med | Med | Med | Med | High | High | High | high> | 15 | 0 | 0 | 0
0 | 7 | Low | Low | Low | Low | Med | Med | Med | Med | High | High | 0 | 0 | 0 | 0 | 0
0 | 6 | Low | Low | Low | Low | Low | Med | Med | Med | Med | High | 0 | 0 | 0 | 0 | 0
0 | 5 | Low | Low | Low | Low | Low | Low | Med | Med | Med | Med | 0 | 0 | 0 | 0 | 0
0 | 4 | Low | Low | Low | Low | Low | Low | Low | Med | Med | Med | 0 | Low | Tolerable, no engineer action required | 0 | 0
0 | 3 | Low | Low | Low | Low | Low | Low | Low | Low | Med | Med | 0 | Med | Undesirable, consider engineer actions to mitigate risk | 0 | 0
0 | 2 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Med | 0 | High | Intolerable, engineering action required | 0 | 0
0 | 1 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Low | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Occurrence | 0 | 0 | 0 | 0 | 0 | Severity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Rating | Occurrence | 0 | Annual Failure Rate | Return Period [years] | 0 | Rating | Severity | Human Safety | 0 | Environment | 0 | WEC Operation | 0 | Assets | 0
0 | 1 | Exceptionally unlikely to occur | 0 | 1e-05 | 100000 | 0 | 1 | Insignificant | Negligible injury, effect on health (e.g. band aid) | 0 | Negligible pollution or no effect on environment | 0 | Negligible effect on performance | 0 | Negligible | 0
0 | 2 | 0 | 0 | 3.1623e-05 | 31600 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [1.5k USD] | 0
0 | 3 | Extremely unlikely to occur | 0 | 0.0001 | 10000 | 0 | 3 | Minor | Minor injuries, health effects (e.g. stitches) | 0 | Minor pollution / slight effect on environment (min disruption on marine life) | 0 | Minor system degradation | 0 | Repairable in-situ, at next maintenance interval [5k USD] | 0
0 | 4 | 0 | 0 | 0.00031623 | 3160 | 0 | 4 | 0 | Moderate injuries and/or health effects (e.g. broken bone) | 0 | 0 | 0 | Moderate system degradation (e.g. loss of MoMo) | 0 | Repairable in-situ, outside maintenance interval (1 day) [15k USD] | 0
0 | 5 | Very unlikely to occur | 0 | 0.001 | 1000 | 0 | 5 | Major | 0 | 0 | Limited levels of pollution, manageable / moderate effect on environment | 0 | 0 | 0 | Repairable in-situ, outside maintenance interval (1 week) [50k USD] | 0
0 | 6 | 0 | 0 | 0.0031623 | 316 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | Major system degradation or loss of operation for 1 month | 0 | [150k USD] | 0
0 | 7 | Rarely expected to occur | 0 | 0.01 | 100 | 0 | 7 | Critical | Hospitalization (with full recovery) | 0 | Moderate pollution (some clean-up costs) / Serious effect on environment | 0 | Major system degradation or loss of operation for 3 months | 0 | Dry dock required for repair [500k USD] | 0
0 | 8 | 0 | 0 | 0.031623 | 31.6 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | Critical system degradation or loss of operation for 6 months | 0 | [1.5M USD] | 0
0 | 9 | One or more during 20 yr lifetime | 0 | 0.1 | 10 | 0 | 9 | Catastrophic | Hospitalization (with lasting disabilities) | 0 | Major pollution (significant clean-up costs) / disastrous effects on the environment | 0 | Failure to generate power for remainder of project, complete failure | 0 | Loss of device [5M USD] | 0
0 | 10 | 0 | 0 | 0.31623 | 3.16 | 0 | 10 | 0 | A fatality | 0 | 0 | 0 | 0 | 0 | 0 | 0