## Data Rights Notice
PROTECTED RIGHTS NOTICE
Use, reproduction, or disclosure is subject to the restrictions in Award No. DE-EE0008627 with the U.S. Department of Energy until July 19, 2024. Business Sensitive Information.

## 0300 System
[13 empty] | Risk Ranking | [11 empty] | Updated Risk Ranking | [11 empty] | 2nd Updated Risk Ranking
0300 Electric Plant FMECA Table | [13 empty] | Severity Class |  |  |  | Risk Class | [7 empty] | Severity Class |  |  |  | Risk Class | [7 empty] | Severity Class |  |  |  | Risk Class
Risk ID | Item Description | Function | Tech. Class | Novel Aspects | Failure Mode | Failure Effects (Local, WEC, System) | Failure Cause(s) | Initial Mode of Operation | Risk Reduction Design | Preventative Detection | Post Failure Detection | Post Failure Repair Strategy (automated, manual) | Occurrence | Human Safety | Environment | Operation | Assets | Human Safety | Environment | Operation | Assets | Recommended Actions | Responsible Party | Actions Taken | Occurrence | Human Safety | Environment | Operation | Assets | Human Safety | Environment | Operation | Assets | 2nd Recommended Actions | Responsible Party (2nd) | Actions Taken (2nd) | Occurrence | Human Safety | Environment | Operation | Assets | Human Safety | Environment | Operation | Assets | Status (open or closed) | Notes
310-1 | Motor Drive | Convert Motor Generator Voltages to DC voltage for transmission and storage. | 2 | Marine application, loading | Short or Open Circuit | Loss of Power Production, PTO Controlled Shutdown may or may not be possible | Corrosion Induced Short Circuit | Normal | Marine Rated system for corrosion protection, controlled nacelle environment | Visual Inspection, SCADA Detection of Flooding | SCADA Diagnosis | In-Situ Inspection, Repair or Replacement | 9 | 1 | 1 | 6 | 5 | Low | Low | Med | Med
310-2 | Motor Drive | Convert Motor Generator Voltages to DC voltage for transmission and storage. | 2 | Marine application, loading | Short or Open Circuit | Loss of Power Production, PTO Controlled Shutdown may or may not be possible | Improper Installation or Manufacturing defect | Normal | V&V (QA/QC) | Visual Inspection | SCADA Diagnosis | In-Situ Inspection, Repair or Replacement of faulty component | 7 | 1 | 1 | 6 | 5 | Low | Low | Med | Med
310-3 | Motor Drive | Convert Motor Generator Voltages to DC voltage for transmission and storage. | 2 | Marine application, loading | Short or Open Circuit | Loss of Power Production, PTO Controlled Shutdown may or may not be possible | Vibration or Buoy Motion induced failure | Normal | V&V (QA/QC), Proper selection of bus attachment system | Visual Inspection | SCADA Diagnosis and visual inspection | In-Situ Inspection, Repair or Replacement of faulty component or mounting | 8 | 1 | 1 | 6 | 5 | Low | Low | Med | Med
310-4 | Motor Drive | Convert Motor Generator Voltages to DC voltage for transmission and storage. | 2 | Marine application, loading | Short Circuit | Loss of Power Production, PTO Controlled Shutdown may or may not be possible | Flooding Induced Failure (contact with water not corrosion) | Normal | System level isolation from water ingress, Marine rated Components, System level seperation of equipment. | Visual Inspection, SCADA Detection of Flooding | SCADA Diagnosis and visual inspection | Removal of Bouy from Water for dry repair or dry dock overhaul | 8 | 1 | 3 | 6 | 7 | Low | Low | Med | Med
330-1 | Energy Storage | Power smoothing for continuous power flow over umbilical to subsea battery, and to support local payload power needs | 2 | Marine application, loading | Faulted Energy Storage | Loss of Power smoothing, Reduced Damping, Reduction in power production to the battery | Corrosion induced failure short/open circuit | Normal | Marine Rated system for corrosion protection, controlled nacelle environment | Visual Inspection, SCADA Detection of Flooding | SCADA Diagnosis | In-Situ Inspection, Repair or Replacement | 9 | 1 | 1 | 5 | 5 | Low | Low | Med | Med
330-2 | Energy Storage | Power smoothing for continuous power flow over umbilical to subsea battery, and to support local payload power needs | 2 | Marine application, loading | Faulted Energy Storage | Loss of Power smoothing, Reduced Damping, Reduction in power production to the battery | Improper Installation or Manufacturing defect | Normal | V&V (QA/QC) | Visual Inspection | SCADA Diagnosis | In-Situ Inspection, Repair or Replacement of faulty component | 7 | 1 | 1 | 5 | 5 | Low | Low | Med | Med
330-3 | Energy Storage | Power smoothing for continuous power flow over umbilical to subsea battery, and to support local payload power needs | 2 | Marine application, loading | Faulted Energy Storage | Loss of Power smoothing, Reduced Damping, Reduction in power production to the battery | Vibration or Buoy Motion induced failure | Normal | V&V (QA/QC), Proper selection of bus attachment system | Visual Inspection | SCADA Diagnosis and visual inspection | In-Situ Inspection, Repair or Replacement of faulty component or mounting | 8 | 1 | 1 | 5 | 5 | Low | Low | Med | Med
330-4 | Energy Storage | Power smoothing for continuous power flow over umbilical to subsea battery, and to support local payload power needs | 2 | Marine application, loading | Faulted Energy Storage | Loss of Power smoothing, Reduced Damping, Reduction in power production to the battery | Flooding Induced Failure (contact with water not corrosion) | Normal | System level isolation from water ingress, Marine rated Components, System level seperation of equipment. | Visual Inspection, SCADA Detection of Flooding | SCADA Diagnosis and visual inspection | Removal of Bouy from Water for dry repair or dry dock overhaul | 8 | 1 | 3 | 5 | 7 | Low | Low | Med | Med
330-5 | Energy Storage | Power smoothing for continuous power flow over umbilical to subsea battery, and to support local payload power needs | 2 | Marine application, loading | Fire/Smoke | Loss of Power smoothing, Reduced Damping, Reduction in power production to the battery | Fire/Smoke induced failure | Normal | Safety and Emergency system smoke alarm, overcurrent protection | Visual Inspection, SCADA Detection of Fire | SCADA Diagnosis and visual inspection | In-Situ Inspection, In-Situ Repair or Replacement of faulty component or Removal of Bouy from Water for dry repair or dry dock overhaul | 7 | 1 | 2 | 5 | 7 | Low | Low | Med | Med
330-5 | Energy Storage | Power smoothing for continuous power flow over umbilical to subsea battery, and to support local payload power needs | 2 | Marine application, loading | Faulted Energy Storage | Loss of Power smoothing, Reduced Damping, Reduction in power production to the battery | Failure of Capacitor internally | Normal | temperature monitoring, charge control. V&V (QA/QC) | Visual Inspection, SCADA Detection | SCADA Diagnosis and visual inspection | In-Situ Inspection, Repair of faulty component | 8 | 1 | 2 | 5 | 5 | Low | Low | Med | Med
340-1 | Umbilical Power Converter | Control power flow over umbilical to subsea battery | 2 | Marine application, loading | Short or Open Circuit | Loss of power transmission across umbilical | Corrosion Induced Short Circuit | Normal | Marine Rated system for corrosion protection, controlled nacelle environment | Visual Inspection, SCADA Detection of Flooding | SCADA Diagnosis | In-Situ Inspection, Repair or Replacement | 9 | 1 | 1 | 6 | 5 | Low | Low | Med | Med
340-2 | Umbilical Power Converter | Control power flow over umbilical to subsea battery | 2 | Marine application, loading | Short or Open Circuit | Loss of power transmission across umbilical | Improper Installation or Manufacturing defect | Normal | V&V (QA/QC) | Visual Inspection | SCADA Diagnosis | In-Situ Inspection, Repair or Replacement of faulty component | 7 | 1 | 1 | 6 | 5 | Low | Low | Med | Med
340-3 | Umbilical Power Converter | Control power flow over umbilical to subsea battery | 2 | Marine application, loading | Short or Open Circuit | Loss of power transmission across umbilical | Vibration or Buoy Motion induced failure | Normal | V&V (QA/QC), Proper selection of bus attachment system | Visual Inspection | SCADA Diagnosis and visual inspection | In-Situ Inspection, Repair or Replacement of faulty component or mounting | 8 | 1 | 1 | 6 | 5 | Low | Low | Med | Med
340-4 | Umbilical Power Converter | Control power flow over umbilical to subsea battery | 2 | Marine application, loading | Short Circuit | Loss of power transmission across umbilical | Flooding Induced Failure (contact with water not corrosion) | Normal | System level isolation from water ingress, Marine rated Components, System level seperation of equipment. | Visual Inspection, SCADA Detection of Flooding | SCADA Diagnosis and visual inspection | Removal of Bouy from Water for dry repair or dry dock overhaul | 8 | 1 | 3 | 6 | 7 | Low | Low | Med | Med
370-1 | Emergency Resistor | Electrical Resistor for dissipating power in over voltage situations | 2 | Marine application, loading | Open circuit occurs in resistor under load | Overvoltage from loss of emergency resistor could damage Electrical Insulation, and result in shorts or open circuits in other components, loss of PTO damping may lead to structural fatigue | Failure due to Corrosion, Inproper Mounting, Vibration, overheating, or over-current | Normal | Marine-rated resistor module, design to provide sufficient cooling and vibration damping | SCADA - temperature, vibration, and current monitoring | SCADA - PTO controller error diagnostics, physical inspection/test | In-Situ Inspection, Repair or Replacement of faulty component | 8 | 1 | 1 | 4 | 5 | Low | Low | Med | Med
380-1 | Motor Bus | Electrical Connection between Generating Motor and Motor Drive | 2 | Marine application, loading | Short Or Open Bus | Loss of Power Generation, PTO Controlled Shutdown | Corrosion Induced Short Circuit | Normal | Marine Rated system for corrosion protection, controlled nacelle environment | Visual Inspection, SCADA Detection of Flooding | SCADA Diagnosis | In-Situ Inspection, Repair or Replacement | 9 | 1 | 1 | 6 | 5 | Low | Low | Med | Med
380-2 | Motor Bus | Electrical Connection between Generating Motor and Motor Drive | 2 | Marine application, loading | Short Or Open Bus | Loss of Power Generation, PTO Controlled Shutdown | Improper Installation or Manufacturing defect | Normal | V&V (QA/QC) | Visual Inspection | SCADA Diagnosis | In-Situ Inspection, Repair or Replacement of faulty component | 7 | 1 | 1 | 6 | 5 | Low | Low | Med | Med
380-3 | Motor Bus | Electrical Connection between Generating Motor and Motor Drive | 2 | Marine application, loading | Short Or Open Bus | Loss of Power Generation, PTO Controlled Shutdown | Vibration or Buoy Motion induced failure | Normal | V&V (QA/QC), Proper selection of bus attachment system | Visual Inspection | SCADA Diagnosis and visual inspection | In-Situ Inspection, Repair or Replacement of faulty component or mounting | 8 | 1 | 1 | 6 | 5 | Low | Low | Med | Med
380-4 | Motor Bus | Electrical Connection between Generating Motor and Motor Drive | 2 | Marine application, loading | Short on Bus | Loss of Power Generation, PTO Controlled Shutdown | Flooding Induced Failure (contact with water not corrosion) | Normal | System level isolation from water ingress, Marine rated Components, System level seperation of equipment. | Visual Inspection, SCADA Detection of Flooding | SCADA Diagnosis and visual inspection | Removal of Bouy from Water for dry repair or dry dock overhaul | 8 | 1 | 3 | 6 | 7 | Low | Low | Med | Med
380-5 | DC Bus | Common electrical connection between motor drive, local energy storage, and umbilical power converter | 2 | Marine application, loading | Short Or Open Bus | Loss of Power Generation, PTO Controlled Shutdown | Corrosion Induced Short Circuit | Normal | Marine Rated system for corrosion protection, controlled nacelle environment | Visual Inspection, SCADA Detection of Flooding | SCADA Diagnosis | In-Situ Inspection, Repair or Replacement | 9 | 1 | 1 | 6 | 5 | Low | Low | Med | Med
380-6 | DC Bus | Common electrical connection between motor drive, local energy storage, and umbilical power converter | 2 | Marine application, loading | Short Or Open Bus | Loss of Power Generation, PTO Controlled Shutdown | Improper Installation or Manufacturing defect | Normal | V&V (QA/QC) | Visual Inspection | SCADA Diagnosis | In-Situ Inspection, Repair or Replacement of faulty component | 7 | 1 | 1 | 6 | 5 | Low | Low | Med | Med
380-7 | DC Bus | Common electrical connection between motor drive, local energy storage, and umbilical power converter | 2 | Marine application, loading | Short Or Open Bus | Loss of Power Generation, PTO Controlled Shutdown | Vibration or Buoy Motion induced failure | Normal | V&V (QA/QC), Proper selection of bus attachment system | Visual Inspection | SCADA Diagnosis and visual inspection | In-Situ Inspection, Repair or Replacement of faulty component or mounting | 8 | 1 | 1 | 6 | 5 | Low | Low | Med | Med
380-8 | DC Bus | Common electrical connection between motor drive, local energy storage, and umbilical power converter | 2 | Marine application, loading | Short on Bus | Loss of Power Generation, PTO Controlled Shutdown | Flooding Induced Failure (contact with water not corrosion) | Normal | System level isolation from water ingress, Marine rated Components, System level seperation of equipment. | Visual Inspection, SCADA Detection of Flooding | SCADA Diagnosis and visual inspection | Removal of Bouy from Water for dry repair or dry dock overhaul | 8 | 1 | 3 | 6 | 7 | Low | Low | Med | Med

## version history
Title | Low Power 8627 Electric Plant FMECA
Doc No | LP-8627-RR-0300
Version | 1.0
Authored | L Rummel
Reviewed | E Amon
Approved Dist.
Approved Final
Version | Date | Summary
1 | 2019-06-13 | Initial draft based on system concept

## set up
| Risk = Occ + Sev | [11 empty] | Note:
| Severity | [11 empty] | - 'set up' and 'linkedPage' are both linked to workbook 'FMECA Master v3.xlsx'
Occ | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  |  | - changes to the tables, risk scores, etc must be made in 'FMECA Master v3.xlsx'
10 | Low | Med | Med | Med | Med | High | High | High | High | High
9 | Low | Low | Med | Med | Med | Med | High | High | High | High | low <= | 11
8 | Low | Low | Low | Med | Med | Med | Med | High | High | High | high> | 15
7 | Low | Low | Low | Low | Med | Med | Med | Med | High | High
6 | Low | Low | Low | Low | Low | Med | Med | Med | Med | High
5 | Low | Low | Low | Low | Low | Low | Med | Med | Med | Med
4 | Low | Low | Low | Low | Low | Low | Low | Med | Med | Med |  | Low | Tolerable, no engineer action required
3 | Low | Low | Low | Low | Low | Low | Low | Low | Med | Med |  | Med | Undesirable, consider engineer actions to mitigate risk
2 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Med |  | High | Intolerable, engineering action required
1 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Low
Occurrence | [5 empty] | Severity
Rating | Occurrence |  | Annual Failure Rate | Return Period [years] |  | Rating | Severity | Human Safety |  | Environment |  | WEC Operation |  | Assets
1 | Exceptionally unlikely to occur |  | 1e-05 | 100000 |  | 1 | Insignificant | Negligible injury, effect on health (e.g. band aid) |  | Negligible pollution or no effect on environment |  | Negligible effect on performance |  | Negligible
2 |  |  | 3.1623e-05 | 31600 |  | 2 | [7 empty] | [1.5k USD]
3 | Extremely unlikely to occur |  | 0.0001 | 10000 |  | 3 | Minor | Minor injuries, health effects (e.g. stitches) |  | Minor pollution / slight effect on environment (min disruption on marine life) |  | Minor system degradation |  | Repairable in-situ, at next maintenance interval [3k USD]
4 |  |  | 0.00031623 | 3160 |  | 4 |  | Moderate injuries and/or health effects (e.g. broken bone) |  |  |  | Moderate system degradation (e.g. loss of function, repairable in-situ) |  | Repairable in-situ, outside maintenance interval (1 day) [5k USD]
5 | Very unlikely to occur |  | 0.001 | 1000 |  | 5 | Major |  |  | Limited levels of pollution, manageable / moderate effect on environment |  |  |  | Repairable in-situ, outside maintenance interval (1 week) [15k USD]
6 |  |  | 0.0031623 | 316 |  | 6 | [5 empty] | Major system degradation or loss of operation for 1 month |  | [25k USD]
7 | Rarely expected to occur |  | 0.01 | 100 |  | 7 | Critical | Hospitalization (with full recovery) |  | Moderate pollution (some clean-up costs) / Serious effect on environment |  | Major system degradation or loss of operation for 3 months |  | Dry dock required for repair [50k USD]
8 |  |  | 0.031623 | 31.6 |  | 8 | [5 empty] | Critical system degradation or loss of operation for 6 months |  | [150k USD]
9 | One or more during 20 yr lifetime |  | 0.1 | 10 |  | 9 | Catastrophic | Hospitalization (with lasting disabilities) |  | Major pollution (significant clean-up costs) / disastrous effects on the environment |  | Failure to generate power for remainder of project, complete failure |  | Loss of device [500k USD]
10 |  |  | 0.31623 | 3.16 |  | 10 |  | A fatality

## linkedPage
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | Risk = Occ + Sev | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Note:
0 | 0 | Severity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - 'set up' and 'linkedPage' are both linked to workbook 'FMECA Master v3.xlsx'
0 | Occ | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 0 | 0 | 0 | 0 | 0 | - changes to the tables, risk scores, etc must be made in 'FMECA Master v3.xlsx'
0 | 10 | Low | Med | Med | Med | Med | High | High | High | High | High | 0 | 0 | 0 | 0 | 0
0 | 9 | Low | Low | Med | Med | Med | Med | High | High | High | High | low <= | 11 | 0 | 0 | 0
0 | 8 | Low | Low | Low | Med | Med | Med | Med | High | High | High | high> | 15 | 0 | 0 | 0
0 | 7 | Low | Low | Low | Low | Med | Med | Med | Med | High | High | 0 | 0 | 0 | 0 | 0
0 | 6 | Low | Low | Low | Low | Low | Med | Med | Med | Med | High | 0 | 0 | 0 | 0 | 0
0 | 5 | Low | Low | Low | Low | Low | Low | Med | Med | Med | Med | 0 | 0 | 0 | 0 | 0
0 | 4 | Low | Low | Low | Low | Low | Low | Low | Med | Med | Med | 0 | Low | Tolerable, no engineer action required | 0 | 0
0 | 3 | Low | Low | Low | Low | Low | Low | Low | Low | Med | Med | 0 | Med | Undesirable, consider engineer actions to mitigate risk | 0 | 0
0 | 2 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Med | 0 | High | Intolerable, engineering action required | 0 | 0
0 | 1 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Low | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Occurrence | 0 | 0 | 0 | 0 | 0 | Severity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Rating | Occurrence | 0 | Annual Failure Rate | Return Period [years] | 0 | Rating | Severity | Human Safety | 0 | Environment | 0 | WEC Operation | 0 | Assets | 0
0 | 1 | Exceptionally unlikely to occur | 0 | 1e-05 | 100000 | 0 | 1 | Insignificant | Negligible injury, effect on health (e.g. band aid) | 0 | Negligible pollution or no effect on environment | 0 | Negligible effect on performance | 0 | Negligible | 0
0 | 2 | 0 | 0 | 3.1623e-05 | 31600 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [1.5k USD] | 0
0 | 3 | Extremely unlikely to occur | 0 | 0.0001 | 10000 | 0 | 3 | Minor | Minor injuries, health effects (e.g. stitches) | 0 | Minor pollution / slight effect on environment (min disruption on marine life) | 0 | Minor system degradation | 0 | Repairable in-situ, at next maintenance interval [3k USD] | 0
0 | 4 | 0 | 0 | 0.00031623 | 3160 | 0 | 4 | 0 | Moderate injuries and/or health effects (e.g. broken bone) | 0 | 0 | 0 | Moderate system degradation (e.g. loss of function, repairable in-situ) | 0 | Repairable in-situ, outside maintenance interval (1 day) [5k USD] | 0
0 | 5 | Very unlikely to occur | 0 | 0.001 | 1000 | 0 | 5 | Major | 0 | 0 | Limited levels of pollution, manageable / moderate effect on environment | 0 | 0 | 0 | Repairable in-situ, outside maintenance interval (1 week) [15k USD] | 0
0 | 6 | 0 | 0 | 0.0031623 | 316 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | Major system degradation or loss of operation for 1 month | 0 | [25k USD] | 0
0 | 7 | Rarely expected to occur | 0 | 0.01 | 100 | 0 | 7 | Critical | Hospitalization (with full recovery) | 0 | Moderate pollution (some clean-up costs) / Serious effect on environment | 0 | Major system degradation or loss of operation for 3 months | 0 | Dry dock required for repair [50k USD] | 0
0 | 8 | 0 | 0 | 0.031623 | 31.6 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | Critical system degradation or loss of operation for 6 months | 0 | [150k USD] | 0
0 | 9 | One or more during 20 yr lifetime | 0 | 0.1 | 10 | 0 | 9 | Catastrophic | Hospitalization (with lasting disabilities) | 0 | Major pollution (significant clean-up costs) / disastrous effects on the environment | 0 | Failure to generate power for remainder of project, complete failure | 0 | Loss of device [500k USD] | 0
0 | 10 | 0 | 0 | 0.31623 | 3.16 | 0 | 10 | 0 | A fatality | 0 | 0 | 0 | 0 | 0 | 0 | 0