## Data Rights Notice
PROTECTED RIGHTS NOTICE
Use, reproduction, or disclosure is subject to the restrictions in Award No. DE-EE0008627 with the U.S. Department of Energy until July 19, 2024. Business Sensitive Information.

## 0560 System
[13 empty] | Risk Ranking | [11 empty] | Updated Risk Ranking | [11 empty] | 2nd Updated Risk Ranking
0560 Cooling System FMECA Table | [13 empty] | Severity Class |  |  |  | Risk Class | [7 empty] | Severity Class |  |  |  | Risk Class | [7 empty] | Severity Class |  |  |  | Risk Class
Risk ID | Item Description | Function | Tech. Class | Novel Aspects | Failure Mode | Failure Effects (Local, WEC, System) | Failure Cause(s) | Initial Mode of Operation | Risk Reduction Design | Preventative Detection | Post Failure Detection | Post Failure Repair Strategy (automated, manual) | Occurrence | Human Safety | Environment | Operation | Assets | Human Safety | Environment | Operation | Assets | Recommended Actions | Responsible Party | Actions Taken | Occurrence | Human Safety | Environment | Operation | Assets | Human Safety | Environment | Operation | Assets | 2nd Recommended Actions | Responsible Party (2nd) | Actions Taken (2nd) | Occurrence | Human Safety | Environment | Operation | Assets | Human Safety | Environment | Operation | Assets | Status (open or closed) | Notes
0560-1 | Cooling Pipes | Contain coolant loop | 1 | none | Large coolant leak | Loss of cooling capacity - resulting in reduced power generation, systems cooling, and/or total PTO systems shutdown | Improper installation or manufacturing defect | Normal | 1) V&V (QC) | Moisture sensors Inspections | 1) SCADA - temperature, pressure, flow sensors, water sensors in nacelle 2) Heat related component failure 3) Visual inspection | In-Situ repair if possible, if not, recover and repair | 6 | 1 | 3 | 6 | 7 | Low | Low | Med | Med
0560-2 | Cooling Pipes | Contain coolant loop | 1 | none | Blockage | Loss or reduction of cooling capacity - resulting in reduced power generation, systems cooling, and/or total PTO systems shutdown | Contamination of cooling circuit | Normal | Filter/screen in cooling circuit. Flush system during commissioning and prevent contamination during installation | Pressure/temperature/flow sensors in cooling circuit | 1) SCADA - temperature, pressure, flow sensors 2) Heat related component failure | In-Situ repair if possible, if not, recover and repair | 7 | 1 | 3 | 5 | 6 | Low | Low | Med | Med
0561-1 | Cooling pumps | Circulate coolant | 1 | none | Electrical Failure | Loss of cooling capacity - resulting in reduced power generation, systems cooling, and/or total PTO systems shutdown | Corrosion induced failure short circuit | Normal | 1) Marine rated components 2) Redundant pumps and controllers | 1) SCADA diagnostics - temperature, pressure, and flow sensors in coolant loop; pump current draw, water intrusion sensors | SCADA Diagnostics, Visual inspection | In-Situ repair if possible, if not, recover and repair | 8 | 1 | 1 | 6 | 7 | Low | Low | Med | Med
0561-2 | Cooling pumps | Circulate coolant | 1 | none | Electrical Failure | Loss of cooling capacity - resulting in reduced power generation, systems cooling, and/or total PTO systems shutdown | Improper installation or manufacturing defect results in failure | Normal | 1) V&V (QC) 2) Redundant pumps and controllers | 1) SCADA diagnostics - temperature, pressure, and flow sensors in coolant loop; pump current draw | SCADA Diagnostics, Visual inspection | In-Situ repair if possible, if not, recover and repair | 7 | 1 | 1 | 6 | 7 | Low | Low | Med | Med
0561-3 | Cooling pumps | Circulate coolant | 1 | none | Electrical Failure | Loss of cooling capacity - resulting in reduced power generation, systems cooling, and/or total PTO systems shutdown | Water induced failure (non-corrosion) | Normal | 1) Marine rated components 2) Redundant pumps and controllers | 1) SCADA diagnostics - water intrusion sensors | SCADA Diagnostics, Visual inspection | In-Situ repair if possible, if not, recover and repair | 8 | 1 | 1 | 6 | 7 | Low | Low | Med | Med
0561-4 | Cooling pumps | Circulate coolant | 1 | none | Electrical Failure | Loss of cooling capacity - resulting in reduced power generation, systems cooling, and/or total PTO systems shutdown | Vibration and/or motion induced failure | Normal | 1) Vibration analysis 2) Equipment and installation designed for dynamic environment 3) Redundant pumps and controllers | 1) SCADA diagnostics - vibration sensors | SCADA Diagnostics, Visual inspection | In-Situ repair if possible, if not, recover and repair | 8 | 1 | 1 | 6 | 7 | Low | Low | Med | Med
0561-5 | Cooling pumps | Circulate coolant | 1 | none | Electrical Failure - smoke/fire | Loss of cooling capacity - resulting in reduced power generation, systems cooling, and/or total PTO systems shutdown | All of the faults 1 thru 4 | Normal | 1) Vibration analysis 2) Equipment and installation designed for dynamic environment 3) Redundant pumps and controllers | 1) SCADA diagnostics - temperature, pressure, and flow sensors in coolant loop; pump current draw, vibration sensors | 1) Smoke alarms - reduce time to electrically isolate 2) Over-current protection - for electrical isolation 3) SCADA Diagnostics 4) Visual inspection | In-Situ repair if possible, if not, recover and repair | 8 | 1 | 1 | 6 | 7 | Low | Low | Med | Med
0562-1 | Cooling pump controllers | Provide electric power to / control cooling pumps | 1 | none | Electrical Failure | Loss of cooling capacity - resulting in reduced power generation, systems cooling, and/or total PTO systems shutdown | Corrosion induced failure short circuit | Normal | 1) Marine rated components 2) Redundant pumps and controllers | 1) SCADA diagnostics - temperature, pressure, and flow sensors in coolant loop; pump current draw, water intrusion sensors | SCADA Diagnostics, Visual inspection | In-Situ repair if possible, if not, recover and repair | 8 | 1 | 1 | 6 | 7 | Low | Low | Med | Med
562-2 | Cooling pump controllers | Provide electric power to / control cooling pumps | 1 | none | Electrical Failure | Loss of cooling capacity - resulting in reduced power generation, systems cooling, and/or total PTO systems shutdown | Improper installation or manufacturing defect results in failure | Normal | 1) V&V (QC) 2) Redundant pumps and controllers | 1) SCADA diagnostics - temperature, pressure, and flow sensors in coolant loop; pump current draw | SCADA Diagnostics, Visual inspection | In-Situ repair if possible, if not, recover and repair | 7 | 1 | 1 | 6 | 7 | Low | Low | Med | Med
0562-2 | Cooling pump controllers | Provide electric power to / control cooling pumps | 1 | none | Electrical Failure | Loss of cooling capacity - resulting in reduced power generation, systems cooling, and/or total PTO systems shutdown | Water induced failure (non-corrosion) | Normal | 1) Marine rated components 2) Redundant pumps and controllers | 1) SCADA diagnostics - water intrusion sensors | SCADA Diagnostics, Visual inspection | In-Situ repair if possible, if not, recover and repair | 8 | 1 | 1 | 6 | 7 | Low | Low | Med | Med
562-3 | Cooling pump controllers | Provide electric power to / control cooling pumps | 1 | none | Electrical Failure | Loss of cooling capacity - resulting in reduced power generation, systems cooling, and/or total PTO systems shutdown | Vibration and/or motion induced failure | Normal | 1) Vibration analysis 2) Equipment and installation designed for dynamic environment 3) Redundant pumps and controllers | 1) SCADA diagnostics - vibration sensors | SCADA Diagnostics, Visual inspection | In-Situ repair if possible, if not, recover and repair | 8 | 1 | 1 | 6 | 7 | Low | Low | Med | Med
0562-3 | Cooling pump controllers | Provide electric power to / control cooling pumps | 1 | none | Electrical Failure - smoke/fire | Loss of cooling capacity - resulting in reduced power generation, systems cooling, and/or total PTO systems shutdown | All of the faults 1 thru 4 | Normal | 1) Vibration analysis 2) Equipment and installation designed for dynamic environment 3) Redundant pumps and controllers | 1) SCADA diagnostics - temperature, pressure, and flow sensors in coolant loop; pump current draw, vibration sensors | 1) Smoke alarms - reduce time to electrically isolate 2) Over-current protection - for electrical isolation 3) SCADA Diagnostics 4) Visual inspection | In-Situ repair if possible, if not, recover and repair | 8 | 1 | 1 | 6 | 7 | Low | Low | Med | Med
0563-1 | Hull Heat Exchanger | Exchange cooling water heat with ocean water | 1 | none | Coolant leak | 1) Flooding 2) Loss of cooling 3) Loss of PTO | Vibration and/or motion induced failure | Normal | 1) Marine design/rated heat exchanger 2) V&V (QC) 3) Heat exchanger mount to inside of hull | none | 1) SCADA - temperature, pressure, flow sensors, water sensors in nacelle 2) Heat related component failure 3) Visual inspection | Recover and repair in drydock | 7 | 1 | 3 | 6 | 7 | Low | Low | Med | Med
0563-2 | Hull Heat Exchanger | Exchange cooling water heat with ocean water | 1 | none | Coolant leak | 1) Flooding 2) Loss of cooling 3) Loss of PTO | Corrosion | Normal | 1) Marine design/rated heat exchanger 2) V&V (QC) 3) Heat exchanger mount to inside of hull | none | 1) SCADA - temperature, pressure, flow sensors, water sensors in nacelle 2) Heat related component failure 3) Visual inspection | Recover and repair in drydock | 8 | 1 | 3 | 6 | 7 | Low | Low | Med | Med

## version history
Title | Low Power 8627 Cooling System FMECA
Doc No | LP-8627-RR-0560
Version | 1
Authored | L Rummel
Reviewed | E Amon
Approved Dist.
Approved Final
Version | Date | Summary
1 | 2019-06-21 | Initial draft based on system concept

## set up
| Risk = Occ + Sev | [11 empty] | Note:
| Severity | [11 empty] | - 'set up' and 'linkedPage' are both linked to workbook 'FMECA Master v3.xlsx'
Occ | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  |  | - changes to the tables, risk scores, etc must be made in 'FMECA Master v3.xlsx'
10 | Low | Med | Med | Med | Med | High | High | High | High | High
9 | Low | Low | Med | Med | Med | Med | High | High | High | High | low <= | 11
8 | Low | Low | Low | Med | Med | Med | Med | High | High | High | high> | 15
7 | Low | Low | Low | Low | Med | Med | Med | Med | High | High
6 | Low | Low | Low | Low | Low | Med | Med | Med | Med | High
5 | Low | Low | Low | Low | Low | Low | Med | Med | Med | Med
4 | Low | Low | Low | Low | Low | Low | Low | Med | Med | Med |  | Low | Tolerable, no engineer action required
3 | Low | Low | Low | Low | Low | Low | Low | Low | Med | Med |  | Med | Undesirable, consider engineer actions to mitigate risk
2 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Med |  | High | Intolerable, engineering action required
1 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Low
Occurrence | [5 empty] | Severity
Rating | Occurrence |  | Annual Failure Rate | Return Period [years] |  | Rating | Severity | Human Safety |  | Environment |  | WEC Operation |  | Assets
1 | Exceptionally unlikely to occur |  | 1e-05 | 100000 |  | 1 | Insignificant | Negligible injury, effect on health (e.g. band aid) |  | Negligible pollution or no effect on environment |  | Negligible effect on performance |  | Negligible
2 |  |  | 3.1623e-05 | 31600 |  | 2 | [7 empty] | [1.5k USD]
3 | Extremely unlikely to occur |  | 0.0001 | 10000 |  | 3 | Minor | Minor injuries, health effects (e.g. stitches) |  | Minor pollution / slight effect on environment (min disruption on marine life) |  | Minor system degradation |  | Repairable in-situ, at next maintenance interval [3k USD]
4 |  |  | 0.00031623 | 3160 |  | 4 |  | Moderate injuries and/or health effects (e.g. broken bone) |  |  |  | Moderate system degradation (e.g. loss of function, repairable in-situ) |  | Repairable in-situ, outside maintenance interval (1 day) [5k USD]
5 | Very unlikely to occur |  | 0.001 | 1000 |  | 5 | Major |  |  | Limited levels of pollution, manageable / moderate effect on environment |  |  |  | Repairable in-situ, outside maintenance interval (1 week) [15k USD]
6 |  |  | 0.0031623 | 316 |  | 6 | [5 empty] | Major system degradation or loss of operation for 1 month |  | [25k USD]
7 | Rarely expected to occur |  | 0.01 | 100 |  | 7 | Critical | Hospitalization (with full recovery) |  | Moderate pollution (some clean-up costs) / Serious effect on environment |  | Major system degradation or loss of operation for 3 months |  | Dry dock required for repair [50k USD]
8 |  |  | 0.031623 | 31.6 |  | 8 | [5 empty] | Critical system degradation or loss of operation for 6 months |  | [150k USD]
9 | One or more during 20 yr lifetime |  | 0.1 | 10 |  | 9 | Catastrophic | Hospitalization (with lasting disabilities) |  | Major pollution (significant clean-up costs) / disastrous effects on the environment |  | Failure to generate power for remainder of project, complete failure |  | Loss of device [500k USD]
10 |  |  | 0.31623 | 3.16 |  | 10 |  | A fatality

## linkedPage
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | Risk = Occ + Sev | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Note:
0 | 0 | Severity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - 'set up' and 'linkedPage' are both linked to workbook 'FMECA Master v3.xlsx'
0 | Occ | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 0 | 0 | 0 | 0 | 0 | - changes to the tables, risk scores, etc must be made in 'FMECA Master v3.xlsx'
0 | 10 | Low | Med | Med | Med | Med | High | High | High | High | High | 0 | 0 | 0 | 0 | 0
0 | 9 | Low | Low | Med | Med | Med | Med | High | High | High | High | low <= | 11 | 0 | 0 | 0
0 | 8 | Low | Low | Low | Med | Med | Med | Med | High | High | High | high> | 15 | 0 | 0 | 0
0 | 7 | Low | Low | Low | Low | Med | Med | Med | Med | High | High | 0 | 0 | 0 | 0 | 0
0 | 6 | Low | Low | Low | Low | Low | Med | Med | Med | Med | High | 0 | 0 | 0 | 0 | 0
0 | 5 | Low | Low | Low | Low | Low | Low | Med | Med | Med | Med | 0 | 0 | 0 | 0 | 0
0 | 4 | Low | Low | Low | Low | Low | Low | Low | Med | Med | Med | 0 | Low | Tolerable, no engineer action required | 0 | 0
0 | 3 | Low | Low | Low | Low | Low | Low | Low | Low | Med | Med | 0 | Med | Undesirable, consider engineer actions to mitigate risk | 0 | 0
0 | 2 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Med | 0 | High | Intolerable, engineering action required | 0 | 0
0 | 1 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Low | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Occurrence | 0 | 0 | 0 | 0 | 0 | Severity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Rating | Occurrence | 0 | Annual Failure Rate | Return Period [years] | 0 | Rating | Severity | Human Safety | 0 | Environment | 0 | WEC Operation | 0 | Assets | 0
0 | 1 | Exceptionally unlikely to occur | 0 | 1e-05 | 100000 | 0 | 1 | Insignificant | Negligible injury, effect on health (e.g. band aid) | 0 | Negligible pollution or no effect on environment | 0 | Negligible effect on performance | 0 | Negligible | 0
0 | 2 | 0 | 0 | 3.1623e-05 | 31600 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [1.5k USD] | 0
0 | 3 | Extremely unlikely to occur | 0 | 0.0001 | 10000 | 0 | 3 | Minor | Minor injuries, health effects (e.g. stitches) | 0 | Minor pollution / slight effect on environment (min disruption on marine life) | 0 | Minor system degradation | 0 | Repairable in-situ, at next maintenance interval [3k USD] | 0
0 | 4 | 0 | 0 | 0.00031623 | 3160 | 0 | 4 | 0 | Moderate injuries and/or health effects (e.g. broken bone) | 0 | 0 | 0 | Moderate system degradation (e.g. loss of function, repairable in-situ) | 0 | Repairable in-situ, outside maintenance interval (1 day) [5k USD] | 0
0 | 5 | Very unlikely to occur | 0 | 0.001 | 1000 | 0 | 5 | Major | 0 | 0 | Limited levels of pollution, manageable / moderate effect on environment | 0 | 0 | 0 | Repairable in-situ, outside maintenance interval (1 week) [15k USD] | 0
0 | 6 | 0 | 0 | 0.0031623 | 316 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | Major system degradation or loss of operation for 1 month | 0 | [25k USD] | 0
0 | 7 | Rarely expected to occur | 0 | 0.01 | 100 | 0 | 7 | Critical | Hospitalization (with full recovery) | 0 | Moderate pollution (some clean-up costs) / Serious effect on environment | 0 | Major system degradation or loss of operation for 3 months | 0 | Dry dock required for repair [50k USD] | 0
0 | 8 | 0 | 0 | 0.031623 | 31.6 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | Critical system degradation or loss of operation for 6 months | 0 | [150k USD] | 0
0 | 9 | One or more during 20 yr lifetime | 0 | 0.1 | 10 | 0 | 9 | Catastrophic | Hospitalization (with lasting disabilities) | 0 | Major pollution (significant clean-up costs) / disastrous effects on the environment | 0 | Failure to generate power for remainder of project, complete failure | 0 | Loss of device [500k USD] | 0
0 | 10 | 0 | 0 | 0.31623 | 3.16 | 0 | 10 | 0 | A fatality | 0 | 0 | 0 | 0 | 0 | 0 | 0