## Set-up
Failure Mode Identification
Project title: | CalWave Ocean Demonstration
System title: | CalWave Scaled Open Water Demonstration System - Xwave
Date: | 2020-09-22
Risk Matrix: | Low | tolerable, no action required
| Medium | mitigation and improvement required to reduce risk
| High | not acceptable: mitigation and improvement required to reduce risk to Low (ALARP)
Probability Classes
No. | Name | Description |  |  | Indicative Annual Failure Rate (up to) | Reference
1 | Very Low | Negligible event frequency |  |  | 0.0001 | Accidental (event not failure)
2 | Low | Event unlikely to occur |  |  | 0.001 | Strength / ULS
3 | Medium | Event rarely expected to occur |  |  | 0.01 | Fatigue / FLS
4 | High | One or several events expected to occur during the lifetime |  |  | 0.1 | Operation low frequency
5 | Very high | One or several events expected to occur each year |  |  | 1 | Operation high frequency
Consequence Classes
Class | Description of consequences (impact on) - Device Level | [5 empty] | Class | Description of consequences (impact on) - Device Level
| Safety | Environment | Operation | Assets | USD |  |  | Safety | Environment | Operation | Assets | USD
1 | Negligible injury, effect on health | Negligible pollution or no effect on environment | Negligible effect on production (hours) | Negligible | 1k |  | 1 | Negligible injury, effect on health | Negligible pollution or no effect on environment | Negligible effect on production (hours) | Negligible | 1k
2 | Minor injuries, health effects | Minor pollution / slight effect on environment (minimum disruption on marine life) | Partial loss of performance (retrieval not required outside maintenance interval) | Repairable within maintenance interval | 10k |  | 2 | Minor injuries, health effects | Minor pollution / slight effect on environment (minimum disruption on marine life) | Partial loss of performance (retrieval not required outside maintenance interval) | Repairable within maintenance interval | 10k
3 | Moderate injuries and/or health effects | Limited levels of pollution, manageable / moderate effect on environment | Loss of performance requiring retrieval outside maintenace interval | Repairable outside maintenance interval | 100k |  | 3 | Moderate injuries and/or health effects | Limited levels of pollution, manageable / moderate effect on environment | Loss of performance requiring retrieval outside maintenace interval | Repairable outside maintenance interval | 100k
4 | Significant injuries | Moderate pollution, with some clean-up costs / Serious effect on environment | Total loss of production up to 1 month | Significant but repairable outside maintenance interval | 1M |  | 4 | Significant injuries | Moderate pollution, with some clean-up costs / Serious effect on environment | Total loss of production up to 1 month | Significant but repairable outside maintenance interval | 1M
5 | A fatality | Major pollution event, with significant clean-up costs / disastrous effects on the environment | Total loss of production greater than 1 month | Loss of device, major repair needed by removal of device and exchange of major components | 10M |  | 5 | A fatality | Major pollution event, with significant clean-up costs / disastrous effects on the environment | Total loss of production greater than 1 month | Loss of device, major repair needed by removal of device and exchange of major components | 10M
Assumptions
Risk Categories
Consequence
Prob. | 1 | 2 | 3 | 4 | 5
5 | Low | Med | High | High | High
4 | Low | Med | Med | High | High
3 | Low | Low | Med | Med | High
2 | Low | Low | Low | Med | Med
1 | Low | Low | Low | Low | Med

## Summary
PRE-MITIGATION | [9 empty] | PRE-MITIGATION
Components and Functions | [5 empty] | Components and Functions |  |  |  | Phases and Activities | [5 empty] | Phases and Activities
| Consequence |  |  |  |  | Total risks | High | Medium | Low |  | Consequence |  |  |  |  | Total risks | High | Medium | Low
Prob. | 1 | 2 | 3 | 4 | 5 | 105 | 7 | 77 | 21 | Prob. | 1 | 2 | 3 | 4 | 5 | 112 | 7 | 58 | 47
5 | 0 | 0 | 0 | 0 | 0 |  | 6.667% | 73.33% | 20% | 5 | 0 | 0 | 0 | 0 | 0 |  | 6.25% | 51.79% | 41.96%
4 | 1 | 2 | 5 | 6 | 0 |  |  |  |  | 4 | 0 | 0 | 0 | 0 | 0
3 | 0 | 3 | 22 | 27 | 1 |  |  |  |  | 3 | 0 | 2 | 16 | 10 | 7
2 | 0 | 2 | 12 | 17 | 4 |  |  |  |  | 2 | 0 | 0 | 42 | 15 | 15
1 | 0 | 0 | 0 | 3 | 0 |  |  |  |  | 1 | 0 | 0 | 3 | 0 | 2
POST-MITIGATION | [9 empty] | POST-MITIGATION
Components and Functions | [5 empty] | Components and Functions |  |  |  | Phases and Activities | [5 empty] | Phases and Activities
| Consequence |  |  |  |  | Total risks | High | Medium | Low |  | Consequence |  |  |  |  | Total risks | High | Medium | Low
Prob. | 1 | 2 | 3 | 4 | 5 | 105 | 0 | 55 | 50 | Prob. | 1 | 2 | 3 | 4 | 5 | 112 | 0 | 43 | 69
5 | 0 | 0 | 0 | 0 | 0 |  | 0% | 52.38% | 47.62% | 5 | 0 | 0 | 0 | 0 | 0 |  | 0% | 38.39% | 61.61%
4 | 1 | 3 | 1 | 0 | 0 |  |  |  |  | 4 | 0 | 0 | 0 | 0 | 0
3 | 0 | 4 | 9 | 6 | 0 |  |  |  |  | 3 | 0 | 3 | 3 | 1 | 0
2 | 0 | 4 | 33 | 31 | 2 |  |  |  |  | 2 | 0 | 1 | 58 | 19 | 12
1 | 0 | 0 | 0 | 8 | 3 |  |  |  |  | 1 | 0 | 0 | 3 | 4 | 8
MITIGATION RESULTS | [9 empty] | MITIGATION RESULTS
Components and Functions | [5 empty] | Components and Functions |  |  |  | Phases and Activities | [5 empty] | Phases and Activities
| Consequence |  |  |  |  | Total risks | High | Medium | Low |  | Consequence |  |  |  |  | Total risks | High | Medium | Low
Prob. | 1 | 2 | 3 | 4 | 5 | 0 | -7 | -22 | 29 | Prob. | 1 | 2 | 3 | 4 | 5 | 0 | -7 | -15 | 22
5 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 5 | 0 | 0 | 0 | 0 | 0
4 | 0 | 1 | -4 | -6 | 0 |  |  |  |  | 4 | 0 | 0 | 0 | 0 | 0
3 | 0 | 1 | -13 | -21 | -1 |  |  |  |  | 3 | 0 | 1 | -13 | -9 | -7
2 | 0 | 2 | 21 | 14 | -2 |  |  |  |  | 2 | 0 | 1 | 16 | 4 | -3
1 | 0 | 0 | 0 | 5 | 3 |  |  |  |  | 1 | 0 | 0 | 0 | 4 | 6
Status:
Components and Functions | [9 empty] | Phases and Activities
Closed | 88 | 83.81% | [7 empty] | Closed | 100 | 89.29%
Open | 17 | 16.19% | [7 empty] | Open | 12 | 10.71%
Total | 105 | [8 empty] | Total | 112
[10 empty] | Anchor Installation | [5 empty] | Anchor Installation
[11 empty] | Consequence |  |  |  |  | Total risks | High | Medium | Low
[10 empty] | Prob. | 1 | 2 | 3 | 4 | 5 | 10 | 0 | 4 | 6
[10 empty] | 5 | 0 | 0 | 0 | 0 | 0 |  | 0% | 40% | 60%
[10 empty] | 4 | 0 | 0 | 0 | 0 | 0
[10 empty] | 3 | 0 | 1 | 0 | 0 | 0
[10 empty] | 2 | 0 | 1 | 4 | 0 | 0
[10 empty] | 1 | 0 | 0 | 0 | 0 | 4

## Components and functions
System: CalWave Scaled Open Water Demonstration System - Xwave
Components and functions
ID |  |  |  | Component | Function | Tech. class | Novelty | Failure mode | Failure mechanism or cause | Detection | Consequence | Current Controls | Risk Ranking |  |  |  | Comments | Recommended Actions | Actions Taken | Action Deadline | Status | Risk Ranking
[13 empty] | Cons. | Prob. | Risk | RPN | [5 empty] | Cons. | Prob. | Risk | RPN
A.0000 |  |  |  | Hull | [16 empty] | open
| A.0100 |  |  | Pressure vessel | [16 empty] | open
|  | A.0101-1 |  | Stiffeners/Beams | Support internal equipment and transmit loads | 2 | Loading uncertainty | Structural failure - Strength | Insufficient or incorrect DLC estimation, FEA or extreme enviornmental condition Improper welding - due to poor welding or improper weld specification | Climate sensors in PTO, pressure and stress sensors on hull (in collaboration with Sandia) | Seawater ingress in PTO compartment PTO disattachment & subsequent failure | Design with maximized safety factors for normal safety Require approved and certified welders and manufactuirng inspections during fabrication | 4 | 2 | Med | 8 |  | Review if increased safety factor on ULS is possible Review weld inspection criteria | Mitigation actions incorporated into build drawings contracts. | 2020-06-15 | Closed | 4 | 2 | Med | 8
|  | A.0101-2 |  | Stiffeners/Beams | Support internal equipment and transmit loads | 2 | Loading uncertainty | Structural failure - Fatigue | Insufficient or incorrect DLC estimation, FEA or extreme enviornmental condition Improper welding | Climate sensors in PTO, pressure and stress sensors on hull (in collaboration with Sandia) | Seawater ingress in PTO compartment PTO disattachment & subsequent failure | Design with maximized safety factors Require weld certificates and inspections during fabrication | 4 | 3 | Med | 12 |  | Review if increased design factor on FLS is possible Review weld inspection criteria | Confirm that with safety factor on ULS, loads are within endurance limit for infinite fatigue life. | 2020-06-15 | Closed | 4 | 2 | Med | 8
|  | A.0101-3 |  | Stiffeners/Beams | Support internal equipment and transmit loads | 2 | Loading uncertainty | Unbalanced forces | Pressure differential due to depth | Visual inspection Strain gauges | Strain in structual beams along many axes | CFD simulation of cases that may cause uneven loading FEA to quantify appropriate safety factor Use alternative beam profiles or patterns where significant off-axis strain is possible Dynamic controls to avoid extreme loads (Hatch) | 4 | 2 | Med | 8 |  | Perform FEA to quantify safety factor Determine if/where strain gauges are feasible Dynamic controls: to identify the design philosophy, how this will be considered for ULS and FLS. Investigate, the failure of the controls (system or component) that could lead to a design condition that, depending on the probability of occurrence, could be considered normal, abnormal or accidental design condition. | Mitigation actions incorporated into build drawings contracts. | 2020-06-15 | Closed | 4 | 2 | Med | 8
|  | A.0101-4 |  | Stiffeners/Beams | Support internal equipment and transmit loads | 2 | Loading uncertainty | Inadequate access for welding, fabrication, and/or assembly | Design not accommodating for fabrication process | Design reviews | Delays and rework, cost | Incorporate fabrication plan into design (i.e. bolt heads in CAD, verify clearance for tools, etc.,) Fabrication plan independently validated | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6
|  | A.0102-1 |  | Pressure Hull | Maintain watertight and structural integrity of internal systems; protection from external enviornment | 2 | Loading uncertainty | Rupture, pintching, sheering of hull sheet | Plastic deformation of shell/hull, e.g. vessel colision, belt connector snapping, PTO wall bent due to overload on winch. Resonance | Tension in lines, loss of buoyancy, loss of PTO Motor torque, Loss of control | Loss of buoyancy, Loss of generator Anchor failure due to increased load Seawater ingress | Increase depth if line tension is determined to have exceeded preset limit | 5 | 2 | Med | 10 |  | Review if increased safety factor on ULS is possible Review weld inspection criteria | Glosten confirmed that lowest expected resonance mode of the hull to be 0.5 Hz from experience, too high for wave frequencies. | 2019-12-15 | Closed | 5 | 1 | Med | 5
|  |  | A.010201-1 | Coatings | Corrision and biofouling control | 2 | Performance of coating and durability | Biofouling buildup on shell | Inadequate biofouling consideration Scratch or imperfection in coating | Periodic visual inspection from vessel | Potential for dynamic effects from weight | Coatings design Sikaflex and/or sacraficial anodes where/as appropriate | 2 | 3 | Low | 6 |  |  |  | N/A | Closed | 2 | 3 | Low | 6
|  |  | A.010201-2 | Coatings | Corrision and biofouling control | 2 | Performance of coating and durability | Corrosion of shell structure | Dissimiliar metals in contact Inadequate corrosion consideration Scratch or imperfection in coating | Periodic visual inspection from vessel | Weakening of hull section, increased potential for structural failure or seawater ingress | Coatings design Periodic visual inspection (drop camera for bottom), ability to pressure wash as needed | 3 | 3 | Med | 9 |  | Determine if N2 backfill is appropriate to avoid internal corrosion Review coatings design with partners and suppliers | After discussing with glosten, internal primer coating deemed to be sufficient. | 3/15/2020 | Closed | 3 | 3 | Med | 9
|  | A.0103-1 |  | PTO Mounting | Structural integrity for PTO system | 2 | Loading uncertainty | Structural failure, connection to B.0000 | Insufficient or incorrect load estimation, FEA or extreme enviornmental condition Error or poor workmanship during assembly, damage during transport | Climate sensors in PTO Visual inspection | Missalignment in PTO belt, damage of PTO belt, Seawater ingress in PTO compartment PTO disattachment & subsequent failure | Design with increased safety factors Quality inspection prior to deployment and after any recovery Verification of weld certificates and quality inspections during assembly Failure of any single PTO will trigger inspection of all PTOs | 4 | 3 | Med | 12 |  | Verify alignment and mounting procedure during PTO bench testing Develop detailed fabrication and assembly plan to address PTO mounting and alignment concerns | Incorporate detalied alignment procedure and allowances into hull assembly plan | 2020-09-01 | Closed | 4 | 2 | Med | 8
|  | A.0103-2 |  | PTO Mounting | Support internal equipment and transmit loads | 2 | Loading uncertainty | Inadequate access for welding, fabrication, and/or assembly | Design not accomidating for fabrication process | Design reviews | Delays and rework, cost | Incorporate fabrication plan into design (i.e. bolt heads in CAD, verify clearance for tools, etc.,) Failure of any single PTO will trigger inspection of all PTOs | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6
|  | A.0105-1 |  | Lifting supports | Provide ability to lift & transport system. Lifting supports to be suitable for use both onshore and offshore (considering side loading on lifting eyes at sea) | 1 | None | Structural failure of lifting point | Inadequate design (lateral loads at sea) Larger than anticipated load | Visual inspection | Inability to safetly lift device | Design for unidirectional loads with adequate safety factors Quality control of lifting points fabrication | 4 | 2 | Med | 8 |  | Review lift and tow points with operational partners | Lift points in hull design according to DNVGL-ST_N001. CalWave to review standard and confirm appropriate implementation. | 6/1/2020 | Closed | 4 | 1 | Low | 4
|  | A.0106-1 |  | PTO/shaft assembly acces hatch | Provide access for mounting and maintenance - conditions for safe transfer to be defined considering device and vessel characteristics | 1 | None | Seawater ingress | Improperly sealed after PTO/shaft assembly | Visual inspection Pressure test | Seawater ingress in PTO compartment PTO failure |  | 4 | 3 | Med | 12 | Need to consider trade-off between rotary seals with low leadage and high friction leading to reduced power production efficiency | Review seal solution with suppliers and partners | Redundant double seal solution For demo unit allowed for higher friction seals, thereby prioritizing lowering risk over power production efficiency | 8/1/2019 | Closed | 4 | 2 | Med | 8
|  | A.0109-1 |  | Hatch Actuation system enclosure | Maintain watertight and structural integrity of internal systems; protection from external enviornment Provide access for maintenance | 1 | Protection from external enviornment (submerged) operation at varied depth) | Seawater ingress | Seal failure Improper closing of hatch after last access | Water detectors Humitidy sensors | Loss of hydraluic controls | Design seal on hatch enclosures with ability to reconstitute and pressure test at sea Design for ability to access necessary components at sea | 4 | 3 | Med | 12 |  | Review suitability of watertight integrity/sealing solution Determine if safe access at sea is feasible Determine if alternatives to access at sea is feasable | Review of hatch actuation watertight integrity | 6/1/2020 | Closed | 4 | 2 | Med | 8
| A.0300 |  |  | Load Mitigation System | [16 empty] | open
|  | A.0301-1 |  | Panels | Reduce effective wave excitation area | 4 | Load transfer to structure Bearing wear-off and fouling | Leak past seals | Inadequate design or improper application | Mooring line tension Hatch position | Unintended load mitigation, operator most likely unaware Corruption of performance data | Review sealing solution with partners and suppliers Determine sealing solution with least complexity in seals | 3 | 3 | Med | 9 |  | Incorporate redundant seal design | Redundant seal solution finalized in collaboration with partners, minimized seal penetrations with updated PTO & shaft design | 10/31/2019 | Closed | 3 | 2 | Low | 6
|  | A.0302-1 |  | Actuation system | Control hatch panels | 3 | operation while submerged loading uncertainty | Fails with hatch closed | Motor failure Mechanical failure of actuation system (due to seized components, failed actuation control or loss of power, biofouling) | Hatch position | Inability to mitigate loads with hatch system | Review passive hatch configuration on loss of power Design for simplified controls, incorporate redundancy where possible | 4 | 3 | Med | 12 |  | Evolve controls to incorporate passive safety mechanism and test during final assembly | No passive opening safety mechanism implemented or planned. Instead, device would dive to depth and await service. | 8/26/2019 | Closed | 3 | 2 | Low | 6
|  | A.0302-2 |  | Actuation system | Control hatch panels | 3 | operation while submerged loading uncertainty | Fails while opening or closing | Motor failure Mechanical failure of actuation system | Hatch position | Inability to recover from load mitigation event Loss of ability to test operational performance until fixed | Overspecify motor to ensure able to close under load | 3 | 3 | Med | 9 |  | Increase safety factor applied to motor | Motor and actuation system not designed to move under all loads, only subset (at least 30% of the time). In the event of a failure, device would dive to depth and await service. | 8/26/2019 | Closed | 3 | 3 | Med | 9
|  | A.0302-3 |  | Actuation system | Control hatch panels | 3 | operation while submerged loading uncertainty | Fails with hatch open | Motor failure Mechanical failure of actuation system | Hatch position | Inability to recover from load mitigation event Loss of ability to test operational performance until fixed | Review passive hatch configuration on loss of power Design for simplified controls, incorporate redundancy where possible | 3 | 3 | Med | 9 |  | Increase safety factor applied to motor | Motor and actuation system not designed to move under all loads, only subset (at least 30% of the time). In the event of a failure, device would dive to depth and await service. | 8/26/2019 | Closed | 3 | 3 | Med | 9
|  | A.0303-1 |  | Guides/Rails | Facilitate hatch panel actuation | 3 | operation while submerged loading uncertainty | Misalignment, jamming | Improper installation Biofouling or corrosion on guides/rails | Hatch position | Inability to fully recover from load mitigation event Inability to fully mitigate loads if needed | Pre-deployment testing of hatch mechanism Devlop alignment procedure with partners and suppliers | 3 | 3 | Med | 9 |  | Include alignment procedure in final design package, update pre-deployment test plan | Detailed alignement procedure evolved. Jamming resistant actuation and linear guide solution selected. | 10/31/2019 | Closed | 3 | 2 | Low | 6
| A.0400 |  |  | Entrapped Water Hull | [16 empty] | open
|  | A.0401-1 |  | Entrapt water outer hull | Increase wet kinematic mass without increasing dry mass | 2 | Protection from external enviornment (submerged) operation at varied depth | Stuctural failure | Large hydrostatic loads putting constant stress on structure (can become unbalanced if partial failure) | Hydrodynamic loads on structure increased and/or unbalanced | Sudden shift of static structural loads | FEA of structural stress moments in static equilibrium Time-domain simulation of motion with unevenly distributed buoyancy Build structure with many evenly distributed buoyancy compartments, using both static buoyancy (foam) and controllable buoyancy (ballast) BIlge pump system to capture fluid in PTO compartment | 4 | 3 | Med | 12 |  | Review and update entrapped water chamber design based on numerical modelling and dynamic simulation results | Updated water entrapment design to be passively acting with distributed fill/drain holes | 1/1/2019 | Closed | 4 | 2 | Med | 8
|  | A.0402-1 |  | Entrapt water fill mechanism (holes) | Increase wet kinematic mass without increasing dry mass | 1 | Protection from external enviornment (submerged) operation at varied depth | Does not fill | Holes clogged | Visual inspection prior to deployment | Higher than planned buoyancy, Higher tension on mooring lines and PTO |  | 3 | 3 | Med | 9 |  | Verify entrapped water chamber functionality in controlled environment (at marina) prior to towing to site. Any time WEC is removed from the water, ensure entrapment chamber holes are cleaned | Visual inspection prior to submergence deemed sufficient action to prevent this failure mode. | 8/26/2019 | Closed | 2 | 2 | Low | 4
|  | A.0402-2 |  | Entrapt water fill mechanism (holes) | Increase wet kinematic mass without increasing dry mass | 1 | Protection from external enviornment (submerged) operation at varied depth | Bottom holes do not drain on recovery | Biofouling | Visual inspection and mooring tension during recovery | Improper buoyancy Additional weight during tow | Determine sufficient anti-fouling coating if/as necessary - in collaboration with naval architect | 3 | 3 | Med | 9 |  | Determine anti-fouling coating in collaboration with naval architect and fabrication contractor | Final decision on anti-fouling coating, redesign of drain holes to be larger slit at bottom. Top air holes may need to be reopened after resurfacing. Bottom holes unlikely to need to be cleared but could be by a diver if needed. | 10/31/2019 | Closed | 3 | 2 | Low | 6
| A.0500 |  |  | Hull Access Covers | [16 empty] | open
|  | A.0501-1 |  | Hatch seal | Control seawater ingress & egress - It is considered that the valves are operated for installation and few adjustments during design life | 2 | Remote operation, consideration for survival case during loss of power/communication event | Seal failure | Corrosion, biofouling Improper installation | Visual inspection | WEC will lose surplus operational positive bouyancy, but remains neutral positive buoyant | Include reisitance to penetration in ballast tank design. | 4 | 1 | Low | 4 |  | Review suitability of watertight integrity/sealing solution Determine if safe access at sea is feasible Determine if alternatives to access at sea is feasable | Review of hatch actuation watertight integrity | 6/1/2020 | Closed | 4 | 1 | Low | 4
B.0000 |  |  |  | PTO | [16 empty] | open
| B.0100 |  |  | Mooring Line Connection | [16 empty] | open
|  | B.0101-1 |  | Belt to Dyneema interface | Translate mooring force to WEC | 2 | Belt drive connection Loading uncertainty Design life / degradation | Mechanical failure | Excessive load Inproper connection (i.e. pin slips out) Fatigue | Mooring line tension | Loss of mooring connection on 1 PTO, Potential slamming of conncetor into hull shell, loss of device | 4 PTO design Develop standard connection procedures Use appropriate safety factor in material selection | 3 | 4 | Med | 12 |  | Increase safety factor applied to sea keeping critical components | Set 2.4 as minimum safety factor | 1/1/2019 | Closed | 3 | 3 | Med | 9
| B.0200 |  |  | Fairlead | [16 empty] | open
|  | B.0201-1 |  | Fairlead Drum | Translate belt force to shaft rotation | 2 | Dynamic motion Loading uncertainty Design life / degradation | Belt seperated from fairlead | Belt slips off the fairlead | Visual inspection | Increased friction on belt, potentially leading to belt failure Surface wear on fairlead and belt | Design with increased safety factors Design belt edges and/or weave pattern to account for potential rubbing on fairlead Design fairlead with guide or similiar | 4 | 3 | Med | 12 |  | Review largest safety factor possible within allowable dimensions, including considering a wider drum Review options for belt weave patterns or material that are best designed to maintain integrity with wear on edges | Cover on fairlead considered to be added to the design to help guide the belt back onto the fairelad in the event of a loss of contact scenario (radial separation concern). Convex crown to be added to fairlead to help with centering and prevent slipping on the edge. | 6/1/2020 | Closed | 4 | 2 | Med | 8
|  | B.0201-2 |  | Fairlead Drum | Translate belt force to shaft rotation | 2 | Dynamic motion Loading uncertainty Design life / degradation | Debris caught in fairlead | Biofouling or other material accumulating on belt | Visual inspection | Increased friction on belt, potentially leading to belt failure Surface wear on fairlead and belt | Design with increased safety factors Design fairlead guide with adequate thickness to allow for some biofouling | 3 | 3 | Med | 9 |  | Review largest safety factor possible within allowable dimensions, including considering a wider drum Review options for belt weave patterns or material that are best designed to maintain integrity with wear on edges | Biofoulding unlikely with frequent excitation. Other debris possible. Incorporate monitoring for belt wrapping on to drum. | 6/1/2020 | Closed | 3 | 3 | Med | 9
|  | B.0201-3 |  | Fairlead Drum | Translate belt force to shaft rotation | 2 | Dynamic motion Loading uncertainty Design life / degradation | Off-axis wrapping of belt | Yaw degree of freedom Inertial lag in rotation of fairlead | Visual inspection | Increased friction on belt, potentially leading to belt failure Surface wear on fairlead and belt | Design fairlead with sufficient dynamic positioning ability to mitigate off-axis belt angles | 4 | 4 | High | 16 |  | Review largest safety factor possible. Review options for belt weave patterns, profiling or material that are best designed to maintain integrity with wear on edges | Engaged external experts to review and mitigate belt wrap angles and dyanmic loading on fairlead; determine sufficient belt/fairlead design and fairlead to drum distance. | 6/1/2020 | Closed | 4 | 3 | Med | 12
|  | B.0202-1 |  | Fairlead Bearing | Translate belt force to shaft rotation | 2 | Dynamic motion Loading uncertainty Design life / degradation | Mechanical failure - seized | Corrosion or biofouling Off axis or excessive loads | Visual inspection | Increased friction on belt, potentially leading to belt failure Surface wear on fairlead and belt | Design with increased safety factors | 4 | 3 | Med | 12 |  | Review largest safety factor possible within allowable dimensions, including considering a wider drum Review options for belt weave patterns or material that are best designed to maintain integrity with wear on edges | Verified safety factor calculations with relevant standards | 6/1/2020 | Closed | 4 | 2 | Med | 8
|  | B.0203-1 |  | Fairlead Bearing Housing | Translate belt force to shaft rotation | 2 | Dynamic motion Loading uncertainty Design life / degradation | Mechanical failure - seized | Seawater ingress into bearing housing Corrosion or biofouling Off axis or excessive loads | Visual inspection | Increased friction on belt, potentially leading to belt failure Surface wear on fairlead and belt | Design with increased safety factors | 4 | 3 | Med | 12 |  | Review largest safety factor possible within allowable dimensions, including considering a wider drum Review options for belt weave patterns or material that are best designed to maintain integrity with wear on edges | Seawater ingress not a concern for sea water lubricated bushings. With that clarification, This item seems redundant with B. 0202-1. | 8/26/2019 | Closed | 4 | 2 | Med | 8
| B.0300 |  |  | Mooring Winch | [16 empty] | open
|  | B.0301-1 |  | Mooring Winch Drum | Translate belt force to shaft rotation | 2 | Dynamic motion (frequency of direction change) Loading uncertainty Design life / degradation | Mechanical failure - seized | Seawater ingress into bearing housing Corrosion or biofouling Off axis or excessive loads | Shaft speed | Recover WEC for repair | Design with increased safety factors | 4 | 3 | Med | 12 |  | Determine if redundant seal or secondary barrier solution is practical | Redundant seal included in shaft design. No plans to test off axis loads on mooring drum. PTO should just be shut down and device recovered. | 8/26/2019 | Closed | 4 | 1 | Low | 4
|  | B.0301-2 |  | Mooring Winch Drum | Translate belt force to shaft rotation | 2 | Dynamic motion (frequency of direction change) Loading uncertainty Design life / degradation | Mechanical failure - freewheeling | Off axis or excessive loads | Shaft torque | Increased load on other PTOs | Design with increased safety factors | 3 | 2 | Low | 6 |  |  | No plans to test off axis loads on mooring drum. PTO should just be shut down and device recovered. Failue in shaft coupling or shaft could also cause this mode. | 8/26/2019 | Closed | 3 | 2 | Low | 6
|  | B.0302-1 |  | Mooring Winch to Belt Drive Attachment (drum termination) | Couple winch to gearbox mechanically | 2 | May be nonstandard winch and/or gearbox Loading uncertainty Design life / degradation | Belt detachment | Excessive load on termination point Inadequate mechanical attachment | Mooring line tension | Loss of mooring connection on 1 PTO | Design for continued operations with 3 PTOs | 4 | 2 | Med | 8 |  | Incorporate learning from PTO bench testing in design review and potential update to belt termination | Connection pin tested with sufficient performance. | 8/26/2019 | Closed | 4 | 2 | Med | 8
|  | B.0303-1 |  | Mooring Drum Shaft Bearings | Provide pressure control to cylinder | 2 | Maintenance vs. degradation Accelerations / motions | Bearing failure - winch drum | Excessive lateral loads Mechanical failure | Shaft torque Difference in shaft torque and power between PTOs, potentially steadily growing offset as bearing deteriorates | Vibration on shaft, potentially leading to cascading failure and seawater ingress if seals fail Siezed shaft at winch, gas spring potentially still operationa | Adequate modelling on shaft loads, particularly lateral loads Sufficient design safety factor | 4 | 2 | Med | 8 |  | Review fairlead design to address lateral load concerns, update control methodology to minimize yaw motion; review options for redundant seals to minimize corrosion risk | Fairlead designed to illiminate lateral loads on mooring drum. NREL responses to shaft bearing reviewed | 8/26/2019 | Closed | 4 | 1 | Low | 4
|  | B.0304-1 |  | Mooring Drum Shaft Seals | Provide watertight integrity at shaft/WEC interface | 2 | Maintenance vs. degradation Accelerations / motions | Leakage past seals | Seal imperfection Corrosion or biofouling around seal | Humitidy sensor in PTO compartments | Seawater ingress in PTO compartments Corrosion or biofouling of internal PTO components | Adequate modelling on shaft loads, particularly lateral loads Sufficient design safety factor Bilge pumps specified to handle minor leakage Redundant seals | 4 | 3 | Med | 12 |  | Determine if redundant seal or secondary barrier solution is practical | Incorporated redundant seal in design | 2019-08-01 | Closed | 4 | 2 | Med | 8
|  | B.0304-2 |  | Mooring Drum Shaft Seals | Provide watertight integrity at shaft/WEC interface | 2 | Maintenance vs. degradation Accelerations / motions | Seal failure - significant seawater ingress | Overpressure or excessive angular load, potentially from misaligned shaft Corrosion or biofouling around seal Seal degredation or distortion | Humitidy sensor in PTO compartments | Seawater ingress in PTO compartments Loss of PTO | Adequate modelling on shaft loads, particularly lateral loads Sufficient design safety factor Compartmentalizing buoyancy chambers Redundant seals | 4 | 4 | High | 16 |  | Determine if redundant seal or secondary barrier solution is practical | Incorporated redundant seal in design | 2019-08-01 | Closed | 4 | 3 | Med | 12
|  | B.0305-1 |  | Mooring Drum Shaft | Provide pressure control to cylinder | 2 | Maintenance vs. degradation Accelerations / motions | Shaft shear | Excessive torque on shaft | Shaft torque | Catastropic failure of PTO, potential for seawater ingress | Modelling of shaft loads verfied on PTO test bench Design safety factor greater than minimum recommended by standards | 4 | 2 | Med | 8 |  | Determine if increased safety factor is approrpate | Shaft shear safety factor of 12 | 2019-07-01 | Closed | 4 | 1 | Low | 4
|  | B.0305-2 |  | Mooring Drum Shaft | Provide pressure control to cylinder | 2 | Maintenance vs. degradation Accelerations / motions | Inadequate access for welding, fabrication, and/or assembly | Design not accomidating for fabrication process | Design reviews | Delays and rework, cost | Incorporate fabrication plan into design (i.e. bolt heads in CAD, verify clearance for tools, etc.,) | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6
|  | B.0305-3 |  | Mooring Drum Shaft | Provide pressure control to cylinder | 2 | Maintenance vs. degradation Accelerations / motions | Tools not available during assembly | Assembly of seals, bearings, etc., may require specialized tools with long lead times | Design reviews | Delays and rework, cost | Incorporate fabrication plan into design (i.e. bolt heads in CAD, verify clearance for tools, etc.,) | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6
| B.0500 |  |  | Motor/Generator | [16 empty] | open
|  | B.0501-1 |  | Motor/Generator | Provide damping to PTO system | 2 | Custom design, load variation | Overheating | Excessive load Inadequate design | Temperature sensors | Reduced range of damping | Verify motor heating profile during PTO bench testing | 4 | 3 | Med | 12 |  | Oversize motor/generator to accomidate unanticipated loads, test motor/generator functionality on PTO test bench Add forced cooling | Convective cooling calculations show adequate cooling without additional forced air | 11/1/2019 | Closed | 3 | 2 | Low | 6
|  | B.0501-2 |  | Motor/Generator | Provide damping to PTO system | 2 | Custom design, load variation | Loss of control - freewheeling | Electrical fault in motor (short circuit in windings) Loss of power/control to motor | Motor current Shaft torque | Loss of depth change function Loss of resonance matching ability Loss of minimum line tension control, leading to higher probability of slack/snap event in mooring line | Specify Motor/Generator with appropriate load specifications and safety factors | 4 | 2 | Med | 8 |  | Oversize motor/generator to accomidate unanticipated loads, test motor/generator functionality on PTO test bench | Motor/Generator characterisation complete and implimented on PTO bench test | 1/1/2019 | Closed | 4 | 2 | Med | 8
|  | B.0501-3 |  | Motor/Generator | Provide damping to PTO system | 2 | Custom design, load variation | Loss of control - seized | Mechanical failure caused by thermal overload Electrical fault in motor (short circuit in windings) | Motor current Shaft torque | High torque on remainder of system | Verify motor load profile during PTO bench testing | 4 | 2 | Med | 8 |  | Oversize motor/generator to accomidate unanticipated loads, test motor/generator functionality on PTO test bench | Motor/Generator characterisation complete and implimented on PTO bench test | 1/1/2019 | Closed | 4 | 2 | Med | 8
|  | B.0502-1 |  | Gearbox | Capture energy, translate to electrical output | 2 | Custom design, load variation | Excessive backlash | Insufficient testing and/or modelling in specifications Inappropriate gearbox selection | Control lag | Inadequate controllability of system | Verify controllability of system during PTO bench testing | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6
|  | B.0502-2 |  | Gearbox | Capture energy, translate to electrical output | 2 | Custom design, load variation | Structural failure | Severe shock load Fatigue | Load sensors | Loss of PTO control (motor/generator no longer driving system) | PTO bench testing of motor and control functionality in high load conditions Duration testing of motor control during PTO bench testing (as much as practical in university lab setting) | 4 | 3 | Med | 12 |  | Oversize motor/generator to accomidate unanticipated loads, test motor/generator functionality on PTO test bench | Motor/Generator characterisation complete and implimented on PTO bench test | 1/1/2019 | Closed | 4 | 2 | Med | 8
|  | B.0502-3 |  | Gearbox | Capture energy, translate to electrical output | 2 | Custom design, load variation | Oil leak | Housing failure Flow mechanism failure | Flow sensors Temperature sensor | Gearbox overheating, leading to increased risk of damage and/or mechanical failure, potentially progressing to a siezed gearbox | PTO bench testing of gearbox both in duration conditions (as much as practical in university lab setting) and high load condiditons | 4 | 1 | Low | 4 |  |  |  | N/A | Closed | 4 | 1 | Low | 4
| B.0600 |  |  | Hydraulic Gas Spring | [16 empty] | open
|  | B.0601-1 |  | Hydraulic Gas Spring | Return PTO to equilibrium position | 2 | Loading uncertainty number of cycles vs. maintenace required | Mechanical failure | Unrelated PTO failure removing damping, or sea state exceeding design range End stop impact Failure of mounting | Stroke position | Shock loads on system | PTO controls verified during PTO bench testing Gas spring oscillation function unit tested prior to full system PTO bench testing and further verified during full-system PTO bench testing | 3 | 3 | Med | 9 | Controls to be verified during PTO bench testing | Fully characterize and test gas spring functionality on PTO test bench | Characterization and full function bench testing of hydraulic pump/motor on upgraded PTO test bench | 11/1/2020 | Open | 3 | 2 | Low | 6
|  | B.0601-2 |  | Hydraulic Gas Spring | Return PTO to equilibrium position | 2 | Loading uncertainty number of cycles vs. maintenace required | Loss of stroke position (oscillating around point other than center of stroke) | Hydraulics system fault Inadvertent buoyancy shift Accumulator fault | Stroke position | Shock loads on system | Gas spring oscillation function unit tested prior to full system PTO bench testing and further verified during full-system PTO bench testing | 3 | 3 | Med | 9 | Controls to be verified during PTO bench testing | Fully characterize and test gas spring functionality on PTO test bench | Characterization and full function bench testing of hydraulic pump/motor on upgraded PTO test bench | 11/1/2021 | Open | 3 | 2 | Low | 6
|  | B.0602-1 |  | Hydraulic Gas Spring | Maintain physical integrity of the gas spring system | 2 | Loading uncertainty number of cycles vs. maintenace required | Mounting failure | Misalignment Inappropriate mounting Excessive vibration | Displacement per force measurements Torque measurements Visual inspection | Accelerated wear on seals Asymmetrical force on shaft | PTO bench testing | 3 | 3 | Med | 9 |  | Verify gas spring mounting procedure and characterize gas spring on PTO test bench | Characterization and full function bench testing of hydraulic pump/motor on upgraded PTO test bench | 11/1/2022 | Open | 3 | 2 | Low | 6
|  | B.0603-1 |  | Hydraulic Gas Spring Shaft Sealing | Maintain physical integrity of the gas spring system | 2 | Loading uncertainty number of cycles vs. maintenace required | Seal failure | Seal imperfection Seal friction or wear | Gas spring pressure Accumulator pressure on high pressure side | Hydraulic oil leak into PTO compartment Degredation of spring function | PTO bench testing Some potential for compensation with HPU Bilge pumps | 3 | 3 | Med | 9 |  | Test material and seal configuration to define wear under different conditions Define by test level of friction and necessary steps to keep friction and wear to reach design life required |  | N/A | Closed | 3 | 2 | Low | 6
|  | B.0604-1 |  | Hydraulic Gas Spring Piston Sealing | Maintain physical integrity of the gas spring system | 2 | Loading uncertainty number of cycles vs. maintenace required | Seal failure | Seal imperfection Seal friction or wear Contamination in cylinder housing | Gas spring pressure Accumulator pressure on high and low pressure sides | Degredation of spring function | PTO bench testing Compensation with HPU | 3 | 3 | Med | 9 |  | Test material and seal configuration to define wear under different conditions Define by test level of friction and necessary steps to keep friction and wear to reach design life required |  | N/A | Closed | 3 | 2 | Low | 6
|  | B.0605-1 |  | Accumulator | Provide pressure control to cylinder | 2 | Maintenance vs. degradation Accelerations / motions | Loss of pressure | Leak Valve failure | Pressure sensor | Improper control of gas spring Increased potential for end stop impact Increased potential for mooring line slack/snap event | Design with appropriate reliability | 3 | 3 | Med | 9 |  | Consider a gas refil system to mitigate losses in air pressure in the accumulator | Adding a compressor to the system determined to be adding more complexity and potential risk than it would mitigate | 1/1/2019 | Closed | 3 | 2 | Low | 6
| B.0700 |  |  | Power electronics | [16 empty] | open
|  | B.0702-1 |  | DC Bus | Provide control for system | 2 | Peak to average load | Bus voltage instability | Connection or communication error Overcurrent Higher than anticipated peak loads | SCADA | Loss or degredation of control | PTO testing Capacitor and brake resistor full system testing | 4 | 3 | Med | 12 |  | Verify loads during PTO test bench Test full system with capacitors, brake resistor and battery connected | Verify loads during PTO test bench Test full system with capacitors, brake resistor and battery connected | 11/1/2019 | Open | 4 | 3 | Med | 12
|  | B.0703-1 |  | Line Side Inverter | Provide control for motor/generator | 2 | Four quadrant control required | Active Line Module failure | Overheating Connection or communication error Vibration Humidity Overcurrent | SCADA | Cannot import power | PTO testing Ensure cabinet is designed with forced cooling and space for air flow Ensure volume to heat calculations support convective heat sink to ocean | 3 | 3 | Med | 9 |  | Verify sufficient convective cooling for electrical components Verify loads during PTO test bench Determine humidity controls (per F.0410-1) Verify overcurrent protection during PTO bench testing Review vibration mounting options and vibration allowances for equipment and determine best solution to minimize risk of vibration caused faults | Large WEC surface area exposed to ocean provides convective cooling beyond power electronic heat generation capacility - fans being incorporated to reduce risk of localized heating Electrical loads validated during PTO bench testing | 5/1/2019 | Closed | 3 | 2 | Low | 6
|  | B.0704-1 |  | Motor Side Inverter | Provide control for motor/generator | 2 | Four quadrant control required | Motor Module failure | Overheating Seawater ingress and/or condensation Electrical short Connection or communication error Vibration Humidity Overcurrent | SCADA | Loss of power system | PTO testing Ensure cabinet is designed with forced cooling and space for air flow Ensure volume to heat calculations support convective heat sink to ocean | 3 | 3 | Med | 9 |  | Verify sufficient convective cooling for electrical components Verify loads during PTO test bench Determine humidity controls (per F.0410-1) Verify overcurrent protection during PTO bench testing Review vibration mounting options and vibration allowances for equipment and determine best solution to minimize risk of vibration caused faults | Large WEC surface area exposed to ocean provides convective cooling beyond power electronic heat generation capacility - fans being incorporated to reduce risk of localized heating Electrical loads validated during PTO bench testing | 5/1/2019 | Closed | 3 | 2 | Low | 6
|  | B.0705-1 |  | Braking Resistor Controller | Dissipate excess power | 1 | None | Failure resulting in short circuit | Improper or loose wiring Incorrect software integration | DC bus voltage | Potential loss of DC bus --> loss of PTO control Fire | Verify brake resistor controller functionality during PTO bench testing Short circuit protection Circuit breakers in MoMo, capacitors, and battery manager | 5 | 2 | Med | 10 |  | Consider dissipating energy with brake resistor on pier (as opposed to inside WEC) thereby allowing operator access to any potential faults. Ensure overcurrent circuit protection between brake resistor and DC bus | Energy being dissipated via umbilical to load on pier Overcurrent protection included in design on both sides of umbilical cable | 5/1/2019 | Closed | 5 | 1 | Med | 5
|  | B.0706-1 |  | Braking Resistor | Dissipate excess power | 1 | None | Overheating resulting in open circuit | Improper specifications - insufficient resistive capacity | DC bus voltage | Loss of braking resistor functionality Loss of WEC performance testing ability until repaired | Climate control in enclosure PTO test bench (determine heat profile) Loss of damping/virtual spring range (net power must =0) | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6
|  | B.0706-2 |  | Braking Resistor | Dissipate excess power | 1 | None | Overheating resulting in increase in ambient temperature in electrical enclosure | Improper specifications | DC bus voltage | Potential loss of power electronics | Climate control in enclosure Separate resistors and PE in separate chambers PTO test bench (determine heat profile) | 3 | 3 | Med | 9 |  | Consider dissipating energy with brake resistor on pier (as opposed to inside WEC) thereby allowing operator access to any potential faults. Ensure overcurrent circuit protection between brake resistor and DC bus | Energy being dissipated via umbilical to load on pier Overcurrent protection included in design on both sides of umbilical cable | 5/1/2019 | Closed | 3 | 2 | Low | 6
|  | B.0707-1 |  | Line Side Contactor | Provide control for motor/generator | 2 | Four quadrant control required | Line Side Contactor tripped (temporary) | Overheating Connection or communication error Vibration Humidity Overcurrent | SCADA | Lose UPS charging Cannot import power | PTO testing Remote reset | 3 | 3 | Med | 9 |  | Test functionality of remotely resetable relatys on PTO test bench | Remote operable relays incorporated in electrical design and tested on PTO test bench | 5/1/2019 | Closed | 2 | 3 | Low | 6
|  | B.0708-1 |  | Motor Side Contactor | Provide control for motor/generator | 2 | Four quadrant control required | Motor Side Contactor tripped (temporary) | Overheating Connection or communication error Vibration Humidity Overcurrent | SCADA | Loss of power system | PTO testing Remote reset | 3 | 3 | Med | 9 |  | Test functionality of remotely resetable relatys on PTO test bench | Remote operable relays incorporated in electrical design and tested on PTO test bench | 5/1/2019 | Closed | 2 | 3 | Low | 6
|  | B.0709-1 |  | Low Voltage Redundant Power System | Backup power source | 1 | None | Insufficient capacity | Improper specifications - insufficient capacity Umbilical cable disconnection Loss of power for extended period | Battery voltage Battery current | Potential Loss of PTO control functionality Improper shutdown of communications on loss of power requiring recovery of WEC to re-establish communications | Design with consideration for uncertainty Pre-programmed soft shutdown PTO bench testing | 4 | 2 | Med | 8 |  | Include on-board battery and UPS for ride through power capability on intermitted loss of communication PTO bench testing to validate communication and control setup Test DC bus system, umbilical cable and connection, and system reaction on loss of external power (umbilical disconnection) prior to deployment | Energy storage included in electrical design PTO test bench validation of communication and control Testing of DC bus storage and reaction to umbilical disconnection | 11/1/2019 | Open | 4 | 2 | Med | 8
|  | B.0709-2 |  | Low Voltage Redundant Power System | Backup power source | 1 | None | Software/communications failure | Improper specifications or incorrect wiring/software integration Loss of communications | Watchdog timer | Lose communication to all controllers | Design for safe shutdown on loss of power and remote restart capability Pre-programmed soft shutdown Isolate/redundant UPS's PTO bench testing | 3 | 4 | Med | 12 |  | Include on-board battery and UPS for ride through power capability on intermitted loss of communication PTO bench testing to validate communication and control setup Test DC bus system, umbilical cable and connection, and system reaction on loss of external power (umbilical disconnection) prior to deployment | Energy storage included in electrical design PTO test bench validation of communication and control Testing of DC bus storage and reaction to umbilical disconnection | 11/1/2019 | Open | 3 | 4 | Med | 12
| B.0800 |  |  | Capacitor Bank | [16 empty] | open
|  | B.0801-1 |  | Capacitors | Maintain stable voltage on DC bus | 2 | Increased degredation from high charge/discharge rates Potential for overvoltage conditions | Capacitor cell imbalance | Physical fault in cell due to degredation Fault in controller software Overheating | Capacitor voltage DC bus voltage | Partial loss of capacitor functionality Partial loss of WEC performance (loss of bus voltage control --> lower torque control range) worst case...can't winch to new depth | PTO bench testing Confirm S120 internal controls Isolate and redundant capacitor stacks Ask vendor for cell balancing | 3 | 4 | Med | 12 |  | Incorporate capacitors and controls in PTO bench testing Engage suppliers to ensure appropriate capacitor setup for operational conditions | Capacitors energized on test bench | 11/1/2019 | Closed | 3 | 3 | Med | 9
|  | B.0801-2 |  | Capacitors | Maintain stable voltage on DC bus | 2 | Increased degredation from high charge/discharge rates Potential for overvoltage conditions | Capacitor failure resulting in open circuit | Cable disconnection Overloading, overvoltage from higher than anticipated power variation on DC bus Overheating | Capacitor voltage DC bus voltage | Loss of capacitor functionality No control over DC bus voltage --> risk of ALM IGBT failure Power for winching bus come from batteries | PTO bench testing | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6
|  | B.0801-3 |  | Capacitors | Maintain stable voltage on DC bus | 2 | Increased degredation from high charge/discharge rates Potential for overvoltage conditions | Capacitor failure resulting in short circuit | Vibration in system from high sea states and/or inadequate mounting Incorrect wiring Overheating | Capacitor voltage DC bus voltage | Potential loss of DC bus Loss motor control entirely Fire | PTO bench testing Short circuit protection Ensure that batteries are isolated | 5 | 2 | Med | 10 |  | PTO test bench to incorporate capcitor integration including test cases with high rate of charge/discharge cycles Incorporate overvoltage & overtemperature safety mechanisms and sensors | Capacitors energized on test bench | 11/1/2019 | Closed | 5 | 1 | Med | 5
|  | B.0801-4 |  | Capacitors | Maintain stable voltage on DC bus | 2 | Increased degredation from high charge/discharge rates Potential for overvoltage conditions | Charge/discharge cycle insufficient to meet load demand | Improper specifications Higher than anticipated load swings on DC bus | Capacitor voltage DC bus voltage | Partial loss of capacitor functionality Partial loss of WEC performance (loss of bus voltage control --> lower torque control range) worst case...can't winch to new depth | Design with consideration for uncertainty PTO bench testing Oversize capacitance | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6
C.0000 |  |  |  | Mooring & Anchoring | [16 empty] | open
| C.0200 |  |  | Mooring Line | [16 empty] | open
|  | C.0201-1 |  | Mooring Line (Dyneema) | Connect device to anchor | 2 | Loading uncertainty | Loss of tension (slack/snap) | Unanticipated environmental conditions | Mooring tension | Shock loads on system (potentially severe) | Incorporated into motor design to maintain minimum line tension. Review of safety factors to understand risk if motor fails to maintain minimum tension Analyze hull response under damage conditions via simulation | 4 | 4 | High | 16 |  | PTO lab testing to validate motor controls Design for structure and mooring/anchor to transition to survival depth with 3 PTOs | 30 mm dyneema selected, with a safety factor of 16 on break strength | 4/1/2019 | Closed | 4 | 2 | Med | 8
|  | C.0201-2 |  | Mooring Line (Dyneema) | Connect device to anchor | 2 | Loading uncertainty | Mechanical failure | Abrasion leading to failure Excessive load | Mooring tension | Loss of mooring connection on 1 PTO Loss of hull stability; excess buoyancy causing list Increased tension in remaining lines | Verify abrasion risk with dynamic modelling Incorporate abrasion protection at potential chaffe points Line stiffness requirements based on minimizing compliance, which has the effect of mechanical load failure safety factor near or greater than 10 | 4 | 3 | Med | 12 | Low probability due to safety factor >10 on mechanical load | PTO lab testing to validate motor controls Design for structure and mooring/anchor to transition to survival depth with 3 PTOs | 30 mm dyneema selected, with a safety factor of 16 on break strength Abrasion protection being added to areas of concern | 4/1/2019 | Closed | 4 | 2 | Med | 8
|  | C.0201-3 |  | Mooring Line (Dyneema) | Connect device to anchor | 2 | Loading uncertainty | Entanglement | Slack line conditions | Mooring tension | Decrease in line length Unbalanced loading Points of concentration loading | Incorporated into motor design to maintain minimum line tension. Review of safety factors to understand risk if motor fails to maintain minimum tension | 4 | 3 | Med | 12 | Taut lines have low probability for entanglement | PTO lab testing to validate motor controls Design for structure and mooring/anchor to transition to survival depth with 3 PTOs | Installation & operations planning iteratively being updated with offshore operations partners to minimize risk of slack lines or entanglement | 8/1/2020 | Closed | 4 | 2 | Med | 8
|  | C.0201-4 |  | Mooring Line (Dyneema) | Connect device to anchor | 2 | Loading uncertainty | Unbalanced pretension in mooring line | Design flaw Unanticipated compliance in PTO Unanticipated sea states Insufficient or incorrect modelling Installation not to tolerance | Mooring tension | Sag in mooring line if unbalance is too large Snap load in mooring tether Misalignment of winch lines Unanticipated hull orientation | Symmetric device design Running simulations with 5-10% difference in fore and aft mooring lines and compare effect on motion, power production and slack lines against baseline case Pretension adjustment through PTO design | 4 | 3 | Med | 12 |  | PTO lab testing to validate motor controls Design for structure and mooring/anchor to transition to survival depth with 3 PTOs | Updated simulations show increased capability to accomidate asymmetry with controls Operations planning updated in collaboration with vessel operators to increase anchor placement accuracy | 4/1/2019 | Closed | 3 | 2 | Low | 6
|  | C.0201-5 |  | Mooring Line (Dyneema) | Connect device to anchor | 2 | Loading uncertainty | Greater than expected yaw motion | Design flaw Unanticipated compliance in PTO Unanticipated sea states Insufficient or incorrect modelling Installation not to tolerance | Mooring tension Unanticipated hull response | Side loading on winches, potentially escalating to winch failure (B.0301 & B.0501) Loss of power production Increase in line tension | Belts used to mitigate fleet angle and CBOS Modelling to determine anticipated yaw | 3 | 3 | Med | 9 |  | PTO lab testing to validate motor controls Design for structure and mooring/anchor to transition to survival depth with 3 PTOs | Updated control methodology to minimize yaw Fairlead design to accomidate lateral forces | 4/1/2019 | Closed | 3 | 2 | Low | 6
|  | C.0201-6 |  | Mooring Line (Dyneema) | Connect device to anchor | 2 | Loading uncertainty | Loss of station keeping | Loss of all four mooring lines | Mooring tension | WEC floating unconstrained Collision with nearby infrastructure/vessels | Geo-fence (GPS) SOP for emergency recovery Navigational markers Hazard lighting when on surface | 5 | 3 | High | 15 |  | PTO lab testing to validate motor controls Design for structure and mooring/anchor to transition to survival depth with 3 PTOs | 30 mm dyneema selected, with a safety factor of >16 on break strength Seakeeping components increased required safety factor 20% (to 2.4) above recommended by standards Transisition to survival depth tested on PTO bench | 4/1/2020 | Closed | 5 | 2 | Med | 10
| C.0300 |  |  | Anchor | [16 empty] | open
|  | C.0301-1 |  | Gravity Anchor | Station keeping, provide seabed reference | 2 | Use existing technology as possible/suitable loading uncertainty cyclic loading geotechnical uncertainty (at least for the 1:4 scale) | Structural failure | Inadequate design Unanticipated failure mechanism and/or load path Inadequate understanding of anchor loads Improper installation Fatigue/degredation | Mooring tension | Loss of station keeping on one PTO Increased potential for slack/snap events | 4 PTO design Design for consequence class 1 (Ref. DNVGL-ST-0119) | 4 | 3 | Med | 12 |  | Increase safety factor due to novelty of application Minimize novelty of design | Obtained sediment samples and lab analyzed to vlidate friction coefficient and internal angle of friction, engaged licensed consultant to assist with anchor design | 10/1/2019 | Closed | 4 | 2 | Med | 8
|  | C.0301-2 |  | Gravity Anchor | Station keeping, provide seabed reference | 2 | Use existing technology as possible/suitable loading uncertainty cyclic loading geotechnical uncertainty (at least for the 1:4 scale) | Non-square anchor grid | Inaccuracies in anchor location during installation Anchor movement after installation Inadequate design Unanticipated failure mechanism and/or load path Excessive line loading | Mooring tension ununiform | Unanticipated angles/loads in mooring & PTO Unanticipated hull response | PTOs ability to compensate with belt length Drum/fairlead able to comply with minimal fleet angle | 3 | 4 | Med | 12 |  | PTO lab testing to validate motor controls Design for structure and mooring/anchor to transition to survival depth with 3 PTOs | Obtained sediment samples and lab analyzed to vlidate friction coefficient and internal angle of friction, engaged licensed consultant to assist with anchor design | 10/1/2019 | Closed | 3 | 2 | Low | 6
|  | C.0302-1 |  | Anchor to Mooring Line Connection (Shackle) | Connect anchor to mooring | 1 | None | Mooring line detachment | Excessive load Inproper connection (i.e. pin slips out) | Mooring line tension | Loss of mooring connection on 1 PTO | 4 PTO design Design for consequence class 1 (Ref. DNVGL-ST-0119) | 4 | 4 | High | 16 |  | Increase safety factor Review operational planning with vessel operators and divers | Seakeeping components increased required safety factor 20% above recommended by standards Working with divers and vessel operators to iteratively update operations planning | 10/1/2019 | Closed | 4 | 3 | Med | 12
|  | C.0303-1 |  | Marker Buoy | Station keeping, provide seabed reference | 1 | Use existing technology as possible/suitable loading uncertainty cyclic loading geotechnical uncertainty (at least for the 1:4 scale) | Loss of marker buoy station keeping | Inadequate design Unanticipated failure mechanism and/or load path Excessive line loading | Mooring tension ununiform | Unanticipated angles/loads in mooring & PTO Unanticipated hull response | PTOs ability to compensate with belt length Drum/fairlead able to comply with minimal fleet angle | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6
D.0000 |  |  |  | SCADA | [16 empty] | open
| D.0100 |  |  | Hull Measurements | [16 empty] | open
|  | D.0102-1 |  | Inertial Measurement Unit (IMU) | Sensor integration - providing situational awareness of sensorized system (speed, force, stroke, etc.,) and ambient environment (temp, humidity, etc.,) | 3 | Submerged device Maintenance reliability operationing ambient | Loss of sensor input Incorrect sensor reading | Sensor mechanical failure Cable or connector failure | SCADA | Loss of situational awareness Errors in control signals, potentially leading to the need to shut-down operation to repair | Design for IMU control redudancy (including critical sensors) | 3 | 4 | Med | 12 |  | Determine potential for redundant or backup controls in the case of IMU failure | Automatic fail-over functionality built into controls where loss of IMU defaults to backup controls Testing of IMU to occur in BP2 | 11/1/2019 | Open | 2 | 4 | Med | 8
|  | D.0107-1 |  | Leak Sensor | Sensor integration - providing situational awareness of sensorized system (speed, force, stroke, etc.,) and ambient environment (pooling water) | 2 | Submerged device Maintenance reliability operationing ambient | Loss of sensor input Incorrect sensor reading | Sensor mechanical failure Cable or connector failure | SCADA | Coming to surface (unnecessarily) during harsh seas | Redundant leak sensors Small time delay before surfacing | 2 | 3 | Low | 6 |  | Test leaks sensors for rsponse time and false alarms prior to deployment | Test leaks sensors for rsponse time and false alarms prior to deployment | 11/1/2020 | Open | 2 | 2 | Low | 4
|  | D.0108-1 |  | Leak Sensor | Sensor integration - providing situational awareness of sensorized system (speed, force, stroke, etc.,) and ambient environment (pooling water) | 2 | Submerged device Maintenance reliability operationing ambient | Actual hull leakage | Failed gaskets, o-rings, or welds | SCADA | Potential leak, could lead to sinking device. |  | 2 | 2 | Low | 4 |  | Test leaks sensors for rsponse time and false alarms prior to deployment Implement delay before coming to State 80. Maybe wait for 15 mins then slowly rise? |  | N/A | Closed | 2 | 2 | Low | 4
|  | D.0108-1 |  | Structural Loads | Sensor integration - providing situational awareness of sensorized system | 2 | Submerged device Maintenance reliability operationing ambient | Loss of sensor input Incorrect sensor reading | Sensor mechanical failure Cable or connector failure | SCADA | Loss of situational awareness | Review fiber bragg installation and configuration with SNL | 2 | 2 | Low | 4 |  | Verify fiber bragg applicability | FBG interrogator from SNL | 11/1/2020 | Open | 2 | 2 | Low | 4
| D.0200 |  |  | PTO Measurements - Electrical/Mechanical | [16 empty] | open
|  | D.0201-1 |  | Mooring Line Tension measured) | Sensor integration - providing situational awareness of sensorized system | 2 | Submerged device Maintenance reliability operationing ambient | Loss of sensor input Incorrect derived value | Sensor mechanical failure Cable or connector failure Error or drift in signal derivation Poor acoustic signal pathway | SCADA | Loss of situational awareness Potential loss of control function | Design for redudancy in controls Validate signal derivation during PTO bench testing | 2 | 4 | Med | 8 |  | Validate signal derivation during PTO bench testing Review options for backup/redundant controls | FAU will design and supply wireless load cell monitoring CalWave will work with FAU to integrate receiver acoustic modem into hull + SCADA. | 11/1/2020 | Open | 2 | 4 | Med | 8
|  | D.0201-1 |  | Mooring Line Tension | Sensor integration - providing situational awareness of sensorized system | 3 | Submerged device Maintenance reliability operationing ambient | Loss of sensor input Incorrect derived value | Sensor mechanical failure Cable or connector failure Error or drift in signal derivation | SCADA | Loss of situational awareness Potential loss of control function | Design for redudancy in controls Validate signal derivation during PTO bench testing | 2 | 4 | Med | 8 |  | Validate signal derivation during PTO bench testing Review options for backup/redundant controls | Test loadpin and acoustics befor device is deployed | 11/1/2020 | Open | 2 | 4 | Med | 8
|  | D.0202-1 |  | Shaft Torque | Sensor integration - providing situational awareness of sensorized system | 2 | Submerged device Maintenance reliability operationing ambient | Loss of sensor input Incorrect derived value | Sensor mechanical failure Cable or connector failure | SCADA | Loss of situational awareness Potential loss of control function | Design for redudancy in controls Validate signal derivation during PTO bench testing | 4 | 4 | High | 16 |  | Determine if redundancy can be built into system | Incorporated torque cell in updated PTO design (no longer a derived signal) - added load cells in two of four mooring lines to verify torque cells | 9/23/2019 | Closed | 4 | 2 | Med | 8
|  | D.0202-2 |  | Shaft Vibration | Sensor integration - providing situational awareness of sensorized system | 2 | Submerged device Maintenance reliability operationing ambient | Loss of sensor input Incorrect encoder signal Overflow of encoder register | Sensor mechanical failure Cable or connector failure | SCADA | Potential loss of situational awareness | Design for reduncancy in monitoring solutions | 3 | 2 | Low | 6 |  |  | Torque cell and encoder signals will be sampled at a high frequency. | 10/28/2019 | Closed | 3 | 2 | Low | 6
|  | D.0203-1 |  | Motor Encoder | Sensor integration - providing situational awareness of sensorized system | 2 | Submerged device Maintenance reliability operationing ambient | Loss of sensor input Incorrect encoder signal Overflow of encoder register | Sensor mechanical failure Cable or connector failure Depth adjustment revolutions exceed register Non-zero starting point on encoder | SCADA | Potential loss of control function Potental loss of depth control | None | 4 | 2 | Med | 8 |  |  |  | N/A | Closed | 4 | 2 | Med | 8
|  | D.0204-1 |  | Gearbox | Speed/torque transformation | 2 | Submerged device Maintenance reliability operationing ambient | Dislodged from mounting Internal tooth failure Broken copupling | Over-torque Over-speed | SCADA | Potential loss of PTO control Potential loss of depth control | Operate in State 90 with 3 PTOs | 4 | 1 | Low | 4 |  |  | Test gearbox on bench | 9/1/2020 | Closed | 4 | 1 | Low | 4
| D.0400 |  |  | Communications | [16 empty] | open
|  | D.0401-1 |  | Acoustic Modem | Sensor integration - providing situational awareness of sensorized system | 2 | Submerged device Maintenance reliability operationing ambient | Loss of sensor input Loss of power/communications Incorrect sensor reading | Connector or wire failure Connection point or service failure | Watchdog timer | Loss of situational awareness Loss of operator input if umbiical is also disconnected or faulted | None; ignore loss of auxiliary signak | 1 | 4 | Low | 4 |  | Test acoustic modem prior to deployment | Acoustic communications cabability will be included with FAU's PADLOC system. | 11/1/2020 | Open | 1 | 4 | Low | 4
| D.0500 |  |  | Controller | [16 empty] | open
|  | D.0501-1 |  | Master Controller | Sensor integration - providing situational awareness of sensorized system | 2 | Submerged device Maintenance reliability operationing ambient | Loss of sensor input Loss of power/communications Incorrect frozen or locked code | Loss of power Undefined inputs confuse state machine | SCADA | Potental loss of PTO control Potential loss of depth control | Onboard actuators fail into safe configuration | 4 | 4 | High | 16 |  | Determine level of redunancy in controls, including dive to survival command Fully test master controller at PTO bench test | Fully test master controller at PTO bench test | 11/1/2020 | Open | 4 | 3 | Med | 12
| D.0800 |  |  | Hatch Monitoring | [16 empty] | open
|  | D.0801-1 |  | Monitoring Sensors | Sensor integration - providing situational awareness of sensorized system | 2 | Submerged device Maintenance reliability operationing ambient | Loss of sensor input Loss of power/communications Incorrect sensor reading | Sensor failure due to seawater ingress Cable or connector failure due to seawater ingress | SCADA | Failure of hatchcontrol equipment, leading to inability to submerge WEC to survival depth | Design for redudancy in controls Design for watertight integrity | 4 | 3 | Med | 12 |  | Review all hull penetrations and determine if redundant sealing solutions possible | Conclusion is to exclude external hatch position sensors. Instead, motors with an absolute encoder will track hatch position. Additionally, the motors will have a torque limit and the rack will include a hard endstop, to ensure the hatchs stay on track. | 8/30/2019 | Closed | 3 | 2 | Low | 6
E.0000 |  |  |  | Electrical Plant | [16 empty] | open
| E.0200 |  |  | Battery Energy Storage | [16 empty] | open
|  | E.0203-1 |  | Batteries | Provide energy storage for device operation when not generating sufficient internal power for auxiliarly loads (comms, bilge system, etc.,) | 1 | None | Short circuit | Improper wiring Internal defects/faults | Bus voltage | Potential loss of DC bus Fire | PTO bench testing Short circuit protection (fuse) | 5 | 2 | Med | 10 |  | Ensure forced air ventallation provided as recommended by battery manufacturer Incorporate and test short circuit protection prior to deployment | Incorporate battery and full DC bus system in PTO bench testing and predeployment checkout Implimented forced cooling in design | 11/1/2019 | Open | 5 | 2 | Med | 10
|  | E.0203-2 |  | Batteries | Provide energy storage for device operation when not generating sufficient internal power for auxiliarly loads (comms, bilge system, etc.,) | 1 | None | Insufficient capacity | Higher hotel loads than anticpated Sustained low sea state | Battery voltage Battery current | Shorten rescue window if the device loses shore power | Design with consideration for uncertainty | 3 | 3 | Med | 9 |  | Verify battery life under differing load conditions | Incorporate and test battery backup endurance into PTO testing | 11/1/2019 | Open | 3 | 3 | Med | 9
|  | E.0203-3 |  | Batteries | Provide energy storage for device operation when not generating sufficient internal power for auxiliarly loads (comms, bilge system, etc.,) | 1 | None | Overcurrent/undervoltage | Higher hotel loads than anticpated Instabilities on DC bus | Battery voltage Battery current | Reliance on 480Vac network for 24V comms power | Rely on commercial charge controller | 4 | 3 | Med | 12 |  | Add isolated 24V power for just comms | Add isolated 24V power for just comms | 11/1/2019 | Open | 4 | 3 | Med | 12
|  | E.0202-1 |  | Battery Charge Controller | Control power flow between batteries and charger/inverters Communication status to main controller | 2 | Voltage transitions | Software/communications failure | Improper specifications Loss of communications | Watchdog timer | More frequent marine operations (cost) and increased down time to recover WEC and/or recharge battery Failures leading to overvoltage or overtemperature could thoretically lead to gassing or fire | Design for safe shutdown on loss of power and remote restart capability PTO bench testing Ensure temperature and gas sensors are includled in battery design | 3 | 3 | Med | 9 |  | Ensure battery suppliers include safety features to include a 120Vac disconnect if overtemperature or overvoltage is indicated | Battery system designed. 3-phase testing scheduled for July/August 2020 | 11/1/2019 | Open | 3 | 3 | Med | 9
F.0000 |  |  |  | Auxilary Systems | [16 empty] | open
| F.0300 |  |  | Hydraulic System | [16 empty] | open
|  | F.0301-1 |  | Hydraulic Power Unit (HPU) | Provide hydraulic pressure | 2 | Actuation mechanism, uncertanity of dynamic loading. Degradation vs. maintenance | Loss of hydraulic pressure in gas spring cylinder and/or accumulator | Hydraulic leak Hydraulic pump or valve failure | Pressure sensor | Inability to maintain gas spring pressure | Go to safety depth | 4 | 2 | Med | 8 |  | Bench test HPU during PTO testing and perform 'as installed' function testing of HPU in WEC prior to deployment | Controls need to be designed to detect this. Gas spring on the affected PTO should be taken offline and motor only control activated. Device should be checked. | 7/28/2020 | Closed | 4 | 2 | Med | 8
| F.0400 |  |  | Internal Climate | [16 empty] | open
|  | F.0401-1 |  | Dehumidifiers | Maintain humidity level in power & electronics enclosure | 2 | Submerged device Reliability vs maintenance Operating ambient | High humidity in enclosure | Sensor failure Condensation beyond anticipated Dehumidifier internal fault Drain tray overfull | Humidity sensor | Loss of power electronics and/or communications Inability to submerge to survival depth | Dehumidifier | 4 | 3 | Med | 12 |  | Determine if dehumidifier is needed or if dessicant packs are sufficient | Dehumidfier caluclated to be unnecessary | 2/1/2020 | Closed | 3 | 3 | Med | 9
|  | F.0403-1 |  | Motor/Generator ventallation | Maintain stable temperature in generator | 2 | Convective cooling w/internal fans for airflow | Motor/Generator overheating | Failure of local fans Significantly higher than anticipated heat generated by motor Significantly warmer seawater | Enclosure temperature sensor | Loss of motor Inability to submerge to survival depth | Forced cooling (fans) local to motor and electronics Convective cooling capable of dissipating +300% of anticipated peak load | 4 | 2 | Med | 8 |  | Determine forced cooling requirements to reduce risk of localized heating near motor/generator and electronics | Cooling calculations completed | 2/1/2020 | Closed | 3 | 2 | Low | 6
|  | F.0404-1 |  | Power electronics ventallation | Maintain stable temperature in power & electronics enclosure | 2 | Convective cooling w/internal fans for airflow | Power electronics overheating | Failure of local fans Significantly higher than anticipated heat generated by motor Significantly warmer seawater | Enclosure temperature sensor | Loss of power electronics Inability to submerge to survival depth | Forced cooling (fans) local to motor and electronics Convective cooling capable of dissipating +300% of anticipated peak load | 4 | 2 | Med | 8 |  | Determine forced cooling requirements to reduce risk of localized heating near motor/generator and electronics | Cooling calculations completed | 2/1/2020 | Closed | 3 | 2 | Low | 6
| F.0500 |  |  | Data logging | [16 empty] | open
|  | F.0501-1 |  | Data Logging | Provide situational awarness for operator and ability to post process data | 2 | Novel concept device | Loss of data logging capability | Lost or insufficient remote download capacity Onboard storage insufficient | SCADA | Corrupt data limiting accuracy of post processed results Lack of ability to accuratly correlate WEC performance with sea states, reduced clarity in test results | Data logging only for post processing, not for real time controls | 2 | 3 | Low | 6 |  |  |  | N/A | Closed | 2 | 3 | Low | 6
|  | F.0501-2 |  | Data Logging | Provide situational awarness for operator and ability to post process data | 2 | Novel concept device | Loss of time syncronization in data logging | Time server not able to keep up with data traffic | SCADA | Corrupt data limiting accuracy of post processed results Lack of ability to accuratly correlate WEC performance with sea states, reduced clarity in test results | Data logging only for post processing, not for real time controls | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6
|  | F.0501-3 |  | Data Logging | Provide situational awarness for operator and ability to post process data | 2 | Novel concept device | Loss of communication with WEC | Loss of power to communication system | SCADA | Loss of control functionality potentially leading to inability to submerge to survival depth | Safety-critical control communications to have at least two independant channels of communications (i.e. cellular, wi-fi, radio frequency, satellite channels) | 4 | 2 | Med | 8 |  | Investigate multiple paths of communication, via umbilical and locally Test during build-out and staging | Communications & SCADA interfaces bench tested and validated on PTO bench test. Wireless communication to be tested locally | 9/1/2020 | Closed | 3 | 2 | Low | 6
|  | F.0501-4 |  | Data Logging | Provide ability for operator to influence device operation | 3 | Novel concept device | Loss of operator visibility/functionality | SCADA overheating | Watchdog timer | Loss of control functionality potentially leading to inability to submerge to survival depth | Design for automatic controls | 4 | 3 | Med | 12 |  | Investigate multiple paths of communication, via umbilical and locally | Communications & SCADA interfaces bench tested and validated on PTO bench test. Wireless communication to be tested locally | 9/1/2020 | Closed | 4 | 2 | Med | 8
G.0000 |  |  |  | Umbilical
| G.0100 |  |  | Export Cable | [16 empty] | open
|  | G.0101-1 |  | Export Cable | Move 480Vac power between WEC and grid | 2 | Uncertainty on dynamic loading Maximum offset seabed touchdown interference with mooring lines | Cable failure | Abraision of jacket - seawater ingress in cable | Communications | Loss of tethered communications potentially leading to inability to submerge to survival depth Loss of power import/export, if extended periods could lead to increased heat load in WEC | Short circuit protection designed in electrical system Sufficient onboard battery for safe shutdown | 4 | 3 | Med | 12 |  | Dynamic modelling (Orcaflex) to determine likely abrasion points and entanglement danger Detailed operations planning to mitigate risk of damage during installation | Orcaflex dynamic modelling in collaboration with NREL | 11/1/2019 | Closed | 4 | 2 | Med | 8
| G.0200 |  |  | Connectors | [16 empty] | open
|  | G.0201-1 |  | WEC-Side Bulkhead Connector | Connect Umbilical to WEC | 2 | Uncertainty on dynamic loading | Connector failure resulting in open ciruit | Unintended loads on connector (particularly side loads) Fatigue Loose or improperly fastened strain termination | Communications | Loss of tethered communications Trip ALM offline Water ingress to WEC Damage to surrounding structure Cannot import power | Orcaflex modelling to determine potential loads on umbilical Additional safety factor on connector Sufficient onboard battery for safe shutdown | 4 | 3 | Med | 12 |  | Dynamic modelling (Orcaflex) to determine likely loading on cable and avoid loading on connectors Detailed operations planning to mitigate risk of damage during installation | Orcaflex dynamic modelling in collaboration with NREL | 11/1/2019 | Closed | 4 | 2 | Med | 8
|  | G.0201-2 |  | WEC-Side Bulkhead Connector | Connect Umbilical to WEC | 2 | Uncertainty on dynamic loading | Connector failure resulting in short circuit | Seawater ingress Improper wiring inside connector | Communications | Loss of tethered communications Fire Trip ALM offline Cannot import power | Short circuit protection designed in electrical system | 4 | 3 | Med | 12 |  | Dynamic modelling (Orcaflex) to determine likely loading on cable and avoid loading on connectors Detailed operations planning to mitigate risk of damage during installation | Orcaflex dynamic modelling in collaboration with NREL | 11/1/2019 | Closed | 4 | 2 | Med | 8
|  | G.0201-3 |  | WEC-Side Bulkhead Connector | Connect Umbilical to WEC | 2 | Uncertainty on dynamic loading | Connector failure resulting in water ingress into WEC hull | Seawater ingress Improper wiring inside connector | Communications | Flooding | Water block on WEC side of connector mounting | 4 | 2 | Med | 8 |  | Review sealing solution with partners | Sealing of connector bulkhead penetrations reviewed with partners | 2020-04-15 | Closed | 4 | 2 | Med | 8
|  | G.0203-1 |  | Cable-Side Connector | Connect Umbilical to WEC | 2 | Uncertainty on dynamic loading | Connector failure resulting in open ciruit | Unintended loads on connector (particularly side loads) | Communications | Loss of tethered communications Trip ALM offline Water ingress to WEC Damage to surrounding structure Cannot import power | Orcaflex modelling to determine potential loads on umbilical Safety factor on connector Sufficient onboard battery for safe shutdown | 4 | 2 | Med | 8 |  | Dynamic modelling (Orcaflex) to determine likely loading on cable and avoid loading on connectors Detailed operations planning to mitigate risk of damage during installation | Orcaflex dynamic modelling in collaboration with NREL | 11/1/2019 | Closed | 4 | 2 | Med | 8
|  | G.0203-2 |  | Cable-Side Connector | Connect Umbilical to WEC | 2 | Uncertainty on dynamic loading | Connector failure resulting in short circuit | Seawater ingress Improper wiring inside connector | Communications | Loss of tethered communications Fire Trip ALM offline Cannot import power | Short circuit protection designed in electrical system | 4 | 2 | Med | 8 |  | Review sealing solution with partners | Sealing of connector bulkhead penetrations reviewed with partners | 2020-04-15 | Closed | 4 | 1 | Low | 4
| G.0300 |  |  | Cable Seakeeping and Anchoring | [16 empty] | open
|  | G.0301-1 |  | Lazy S configuration | Provide for slack in umbilical to allow for depth change operation and dynamic motions while preventing entanglement and maintaining umbilical load & bending requirements | 2 | Uncertainty on kinematics | Entanglement with winch, mooring lines or anchor. | Umbilical pulled into PTO winch due to excessive surge motion, entangled with mooring lines due to excessive yaw motion, entangled with anchor due to excessive heave motion. Caused by incorrect design of Lazy S or buoyancy module coming loose, potentially leading to a loss of umbilical communication and power connectivity | Communications | Loss of tethered communications Fire Trip ALM offline Cannot import power | Short circuit protection designed in electrical system | 4 | 3 | Med | 12 |  | Perform dynamic modelling (orcaflex) of umbilical cable kinematics to mitigate strain on cable and potential for interaction with WEC and/or mooring lines | Orcaflex dynamic modelling in collaboration with NREL | 11/1/2019 | Closed | 4 | 2 | Med | 8
|  | G.0301-2 |  | Lazy S configuration | Provide for slack in umbilical to allow for depth change operation and dynamic motions while preventing entanglement and maintaining umbilical load & bending requirements | 2 | Uncertainty on kinematics | Fatigue/Abrasion | Umbilical in contact with mooring line, WEC hull, or abraiding against cable anchor connection points | Communications | Loss of tethered communications Fire Trip ALM offline Cannot import power | Short circuit protection designed in electrical system | 4 | 3 | Med | 12 |  | Perform dynamic modelling (Orcaflex) of umbilical cable kinematics to mitigate strain on cable and potential for interaction with WEC and/or mooring lines | Orcaflex dynamic modelling in collaboration with NREL | 11/1/2019 | Closed | 4 | 2 | Med | 8

## Phases and activities - HAZID
System: CalWave Scaled Open Water Demonstration System - Xwave
Phases and activities
Phases and activities
ID |  |  | Activity | Description | Tech Class | Novelty | Failure mode | Failure mechanism or cause | Detection | Consequence | Current Controls | Risk Ranking |  |  |  | Comments | Recommended Actions | Actions Taken | Action Deadline | Status | Risk Ranking |  |  |  | Operational Procedure (v4.1)
[12 empty] | Cons. | Prob. | Risk | RPN | [5 empty] | Cons. | Prob. | Risk | RPN
| X.0000 |  | Programmatic | [16 empty] | open
|  | X.0010.1 | Program delay | Design for appropriate lifting points to allow for crane handling, both prior to full assembly and post assembly | 2 | Device geometry and center of gravity - determined by CAD model, but must be verified experimentally | Not prepared to deploy at scheduled test site time | WEC not ready in time PTO test bench delayed, leading to delay in data leading to final design Schedule conflicts with test site | Program schedule | Increased cost in staff, test site Partial loss in credibility Seasonal variation of ocean climate at test site | Periodic scheuled reviews with internal team, funders, test site, partners, and subcontractors Early detection and mitigation of any schedule delays | 3 | 3 | Med | 9 |  | Secure operational permits that extend beyond scheduled period Plan for operating conditions beyond scheduled period | Permit applications extend to 2021 Survival sea states including winter | N/A | Closed | 2 | 3 | Low | 6 | N/A
|  | X.0020.1 | Program over budget | Design for appropriate lifting points to allow for crane handling, both prior to full assembly and post assembly | 2 | Device geometry and center of gravity - determined by CAD model, but must be verified experimentally | Insufficient remaining funds at time of deployment | Program delays increasing cost Insufficient budget estimates | Program budget | Reduction in scope may be required Increased cost in staff, test site Partial loss in credibility | Periodic budget reviews with internal team, funders, test site, partners, and subcontractors Early detection and mitigation of any budget delays | 3 | 3 | Med | 9 |  | Plan & budget for multiple device recoveries for planned updates to also include corrective service | Budget anticipates mid-test device recoveries and inspections | N/A | Closed | 3 | 3 | Med | 9 | N/A
| X.0100 |  | Transportation of device to test site | [16 empty] | open
|  | X.0110.1 | Lifting device with crane | Design for appropriate lifting points to allow for crane handling, both prior to full assembly and post assembly | 2 | Device geometry and center of gravity - determined by CAD model, but must be verified experimentally | Lifting eye mechanical failure | Overloading of lifting eye Inproperly designed lifting eye Directional loading on lifting eye | Visual inspection | Personel injury Damage to WEC | Incorporate transportation logistics into hull design SOP to inspect all lifting equipment periodically and prior to use. All equipment used shall be appropriate for the operation and come with valid certificates (or similar). | 5 | 2 | Med | 10 | All lift points, rigging etc. should be designed, manufactured and inspected according to DNVGL-ST-N001 See Table 5-11 for fabrication inspection requirements. Other inspection requirements are in Section 16. | Lifting eye design review with naval architect and operational partners | All lift points reviewed per specifications | 2020-06-15 | Closed | 5 | 1 | Med | 5 | Fabrication & Assembly Plan
|  | X.0110.2 | Lifting device with crane | Design for appropriate lifting points to allow for crane handling, both prior to full assembly and post assembly | 2 | Device geometry and center of gravity - determined by CAD model, but must be verified experimentally | Lifting equipment failure | Large angle on slings Inadequate lift plan Lifting equipment not properly inspected | Visual inspection | Personel injury Damage to WEC | SOP to inspect all lifting equipment periodically and prior to use. All equipment used shall be appropriate for the operation and come with valid certificates (or similar). | 5 | 2 | Med | 10 | All lift points, rigging etc. should be designed, manufactured and inspected according to DNVGL-ST-N001 See Table 5-11 for fabrication inspection requirements. Other inspection requirements are in Section 16. | Verify device center of gravity and include lift plans in operational planning | All lift points reviewed per specifications | 2020-06-15 | Closed | 5 | 1 | Med | 5 | Fabrication & Assembly Plan
|  | X.0110.3 | Lifting device with crane | Design for appropriate lifting points to allow for crane handling, both prior to full assembly and post assembly | 2 | Device geometry and center of gravity - determined by CAD model, but must be verified experimentally | Insufficient or inappropriatly placed lifting eyes | Insufficient lift plan incorporated into hull design | Visual inspection | Personel injury Damage to WEC | Incorporate transportation logistics into hull design SOP to inspect all lifting equipment periodically and prior to use. All equipment used shall be appropriate for the operation and come with valid certificates (or similar). | 5 | 2 | Med | 10 | All lift points, rigging etc. should be designed, manufactured and inspected according to DNVGL-ST-N001 See Table 5-11 for fabrication inspection requirements. Other inspection requirements are in Section 16. | Lifting eye design review with naval architect and operational partners | All lift points reviewed per specifications | 2020-06-15 | Closed | 5 | 1 | Med | 5 | Fabrication & Assembly Plan
|  | X.0120.1 | Road transportation | Design for road transportation | 2 | Device geometry and weight. Demonstration scale device to be designed for road transport. Full scale will need to be fabricated or assembled at harbour and barge transported due to size. | Inability to cost effectively transport WEC | Transportation logistics not incorporated into hull design | Visual inspection | Delay in transportation Cost of modifications | Incorporate transportation logistics into hull design | 3 | 2 | Low | 6 |  | Road transport tie down points should be examined after use to ensure no damage has occurred. |  | N/A | Closed | 3 | 2 | Low | 6 | Fabrication & Assembly Plan
|  | X.0120.2 | Road transportation | Design for road transportation | 2 | Device geometry and weight. Demonstration scale device to be designed for road transport. Full scale will need to be fabricated or assembled at harbour and barge transported due to size. | Inability to physically secure WEC for transport | Tie down points not incorporated into hull design | Visual inspection | Delay in transportation Cost of modifications | Incorporate transportation logistics into hull design | 3 | 2 | Low | 6 |  | Road transport tie down points should be examined after use to ensure no damage has occurred. |  | N/A | Closed | 3 | 2 | Low | 6 | Fabrication & Assembly Plan
|  | X.0120.3 | Road transportation | Design for road transportation | 2 | Device geometry and weight. Demonstration scale device to be designed for road transport. Full scale will need to be fabricated or assembled at harbour and barge transported due to size. | Stability of WEC during transport | Excessive wind during transport | Visual inspection | Program delays Damage to WEC | Incorporate transportation logistics into hull design | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | Fabrication & Assembly Plan
|  | X.0121.1 | Fluids | Ensure any internal fluids are drained or allowable | 1 | None | Fluid spill during transport | Fluid systems inadequatly secured or drained | Visual inspection | Enviornmental impact Human safety | SOPs to include fluid systems secured or drained prior to transport | 3 | 1 | Low | 3 |  |  |  | N/A | Closed | 3 | 1 | Low | 3 | Fabrication & Assembly Plan
|  | X.0122.1 | Chemicals | Ensure any internal chemical (i.e. batteries) are removed, discharged, or otherwise allowable | 1 | None | Chemical spill during transport | Batteries inadequatly secured or discharged | Visual inspection | Enviornmental impact Human safety | SOPs to include batteries to be secured or discharged prior to transport | 3 | 1 | Low | 3 |  |  |  | N/A | Closed | 3 | 1 | Low | 3 | Fabrication & Assembly Plan
| X.0200 |  | Anchor installation | [16 empty] | open
|  | X.0210.2 | Transport to harbor | Transport fabricated anchor to harbor | 1 | None | Failure of lifting point(s) during lift | Insufficient or improperly placed lifting points | Visual inspection | Personel injury Damage to anchor | Incorporate transportation logistics into anchor design SOP to inspect all lifting equipment periodically and prior to use. All equipment used shall be appropriate for the operation and come with valid certificates (or similar). | 5 | 2 | Med | 10 | All lift points, rigging etc. should be designed, manufactured and inspected according to DNVGL-ST-N001 See Table 5-11 for fabrication inspection requirements. Other inspection requirements are in Section 16. | Minimize novelty of anchor design Design review of lifting points Detailed lift plan and review with vessel operators | Lift points designed for greater of dry weight and wet weight plus anticipated seafloor suction. Simplified steel design incorporated and reviewed with licensed engineer | 2020-03-15 | Closed | 5 | 1 | Med | 5 | N/A
|  | X.0220.1 | Transport to harbor | Transport fabricated anchor to harbor | 1 | None | Lifting equipment failure | Large angle on slings Inadequate lift plan Lifting equipment not properly inspected | Visual inspection | Personel injury Damage to WEC | SOP to inspect all lifting equipment periodically and prior to use. All equipment used shall be appropriate for the operation and come with valid certificates (or similar). | 5 | 1 | Med | 5 | All lift points, rigging etc. should be designed, manufactured and inspected according to DNVGL-ST-N001 See Table 5-11 for fabrication inspection requirements. Other inspection requirements are in Section 16. | Minimize novelty of anchor design Design review of lifting points Detailed lift plan and review with vessel operators | Lift points designed for greater of dry weight and wet weight plus anticipated seafloor suction. Simplified steel design incorporated and reviewed with licensed engineer | 2020-03-15 | Closed | 5 | 1 | Med | 5 | N/A
|  | X.0220.2 | Transport from harbor to vessel | Lift from pier to vessel | 1 | None | Failure of lifting point(s) during lift | Insufficient or improperly placed lifting points | Visual inspection | Personel injury Damage to anchor | Incorporate transportation logistics into anchor design SOP to inspect all lifting equipment periodically and prior to use | 5 | 2 | Med | 10 |  | Minimize novelty of anchor design Design review of lifting points Detailed lift plan and review with vessel operators | Lift points designed for greater of dry weight and wet weight plus anticipated seafloor suction. Simplified steel design incorporated and reviewed with licensed engineer | 2020-03-15 | Closed | 5 | 1 | Med | 5 | 9.2
|  | X.0220.3 | Transport from harbor to vessel | Lift from pier to vessel | 1 | None | Lifting equipment failure | Large angle on slings Inadequate lift plan Lifting equipment not properly inspected | Visual inspection | Personel injury Damage to anchor | SOP to inspect all lifting equipment periodically and prior to use | 5 | 1 | Med | 5 |  | Minimize novelty of anchor design Design review of lifting points Detailed lift plan and review with vessel operators | Lift points designed for greater of dry weight and wet weight plus anticipated seafloor suction. Simplified steel design incorporated and reviewed with licensed engineer | 2020-03-15 | Closed | 5 | 1 | Med | 5 | 9.2
|  | X.0230.1 | Transport from harbor to vessel | Lift from pier to vessel | 1 | None | Weather delays | Weather not suitable for shore or vessel crane operations | Lifting plan | Delays, cost | SOP to identify weather windows for crane operations Schedule delivery of anchors from fabricators with weather considerations | 3 | 3 | Med | 9 |  | Minimize novelty of anchor design Design review of lifting points Detailed lift plan and review with vessel operators | Lift points designed for greater of dry weight and wet weight plus anticipated seafloor suction. Simplified steel design incorporated and reviewed with licensed engineer | 2020-03-15 | Closed | 3 | 2 | Low | 6 | 9.2
|  | X.0230.2 | Lower anchor to seafloor | Install anchor in appropriate location, ensuring with vessel GPS that anchors are installed within geometry requirements | 1 | Anchor connection point to be withing +/- 1.5m of intended position | Incorrect anchor placement | Inadequate vessel stationkeeping during operation Inadequate crane handling during operation Mooring line incorrect length | Vessel GPS ROV verfication | Unsymmetric mooring angles, leading to unknown and unintended load profiles in PTOs and unanticipated dynamics in performance results | Maximize allowable anchor offset in design Determine allowable anchor offset in modelling Review install procedure with vessel operators early in process | 3 | 3 | Med | 9 |  | Determine required accuracy for anchor placement Define measurement equipment for location of anchors and associated level of accuracy | Incorporate required accuracy and how to appropriately measure (e.g. accuracy of gps & how to record) into planning |  | Open | 3 | 2 | Low | 6 | 9.2
|  | X.0240.1 | Lower anchor to seafloor | Install anchor in appropriate location, ensuring with vessel GPS that anchors are installed within geometry requirements | 1 | Anchor connection point to be withing +/- 1.5m of intended position | Anchor not level on seafloor | Unanticipated seafloor objects or benthic properties | Dive survey & ROV | Additional operations to correctly place anchor Potential damage to anchor | Drop camera or dive/ROV survey of seafloor prior to operation | 2 | 3 | Low | 6 |  | Determine required accuracy for anchor placement Define measurement equipment for location of anchors and associated level of accuracy | Incorporate required accuracy and how to appropriately measure (e.g. accuracy of gps & how to record) into planning |  | Open | 2 | 2 | Low | 4 | 9.2
|  | X.0240.2 | Buoy off mooring line | Provide navigational marker, keep mooring lines taunt and allow for mooring line pickup | 2 | Potentially use a bridal to coallate four mooring lines to ensure lines are maintained taunt and mark center point of mooring grid for device installation | Dropped line (or other equipment) Buoy does not stay on surface, inappropriate navigational light | Human error Weather Buoy inappropriate for intended use | Installation plan | Dive operation required to recover dropped line or equipment | Review O&M procedures with local marine operators and appropriate authorities (test site, harbors, etc.,) | 3 | 2 | Low | 6 | Review with other stakeholders should be done as early as possible to avoid future rework. |  |  |  | Open | 3 | 2 | Low | 6 | 9.2
|  | X.0250.1 | Dive operations | Provide navigational marker, keep mooring lines taunt and allow for mooring line pickup | 2 | Potentially use a bridal to coallate four mooring lines to ensure lines are maintained taunt and mark center point of mooring grid for device installation | Personel safety and proper planning for dive operations | Inadequate prior planning for any necessary dive operations | Installation plan | Delays, additional cost | Dive operation not intended for anchor installation Installation plan to indentify causes for dive operations Local dive team consulted in order to minimize spin up time if required | 3 | 2 | Low | 6 |  |  |  |  | Open | 3 | 2 | Low | 6 | 9.2
|  | X.0260.1 | Reposition anchor | Use lift bags and divers to reposition anchor(s) should it be determined necessary | 2 | Use of lift bags in repositioning, sufficiently sized vessels for lifting not economically available | Personel safety and proper planning for dive operations | Inadequate prior planning for any necessary dive operations | Installation plan | Delays, additional cost Inability to accuratly achieve anchor position | Review O&M procedures with local marine operators and appropriate authorities (test site, harbors, etc.,) | 3 | 3 | Med | 9 |  | Optimize controls to minimize impact of minor inaccuracies in anchor placement |  |  | Open | 2 | 3 | Low | 6 | 9.2
| X.0300 |  | Umbilical installation | [16 empty] | open
|  | X.0310.1 | Umbilical accessories (for lazy S, etc.,) | Use appropriate modelling tool (Orcaflex) to verify umbilical dynamics and determine approprate lay pattern to maintain MBR | 2 | None (for demonstration will be site dependant) | Exceeding bending radius | Accessories creating excessive bending in mooring line | ROV or Drop Camera | Damage to umbilical | Review lay plan with vessel operators Model dynamic motion of umbilical with accessories (orcaflex) | 4 | 3 | Med | 12 |  | Dynamic modelling of umbilical cable configuration Review install plan with local operators and pre-deployment HAZID | Performed Ocraflex dynamic modelling of various sea states | 05/15/2020 | Closed | 4 | 2 | Med | 8 | 9.5
|  | X.0310.2 | Umbilical accessories (for lazy S, etc.,) | Use appropriate modelling tool (Orcaflex) to verify umbilical dynamics and determine approprate lay pattern to maintain MBR | 2 | None (for demonstration will be site dependant) | Accessories fall off | Accessories not adequatly secured | ROV or Drop Camera | Umbilical not adeqatly secured, leading to damage to umbilical | Secure buoyancy modules with wratchet straps or other additional securing measures | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 9.5
|  | X.0311.1 | Umbilical installation procedures | Determine where/how umbilical will be laid and picked up by vessel to formulate lay plan and any necessary bend restrictors, etc., | 2 | None (for demonstration will be site dependant) | Exceeding bending radius | Lay plan does not adequatly consider lay angles Vessel does not adequatly follow lay plan | Vessel GPS Drop camera | Damage to umbilical | Review lay plan with vessel operators Use cable protection where appropriate | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 9.5
|  | X.0311.2 | Umbilical installation procedures | Determine where/how umbilical will be laid and picked up by vessel to formulate lay plan and any necessary bend restrictors, etc., | 2 | None (for demonstration will be site dependant) | Abrasion of cable | Cable rubs on abrasive element (external equipment, sea floor, water column) | Drop camera | Damage to umbilical | Review lay plan with vessel operators Use cable protection where appropriate | 4 | 3 | Med | 12 |  | Dynamic modelling of umbilical cable configuration Review install plan with local operators and pre-deployment HAZID | Performed Ocraflex dynamic modelling of various sea states | 05/15/2020 | Closed | 4 | 2 | Med | 8 | 9.5
| X.0400 |  | Craning WEC from pier to vessel/quayside | [16 empty] | open
|  | X.0410.1 | Lifting device with crane | Use either vessel crane or pier crane to transfer device from pier to installation vessel | 1 | None (device will have been previously lifted during transportation) | Lifting eye mechanical failure | Overloading of lifting eye Inproperly designed lifting eye Directional loading on lifting eye | Visual inspection | Personel injury Damage to WEC | Incorporate transportation logistics into hull design SOP to inspect all lifting equipment periodically and prior to use | 5 | 2 | Med | 10 | All lift points, rigging etc. should be designed, manufactured and inspected according to DNVGL-ST-N001 See Table 5-11 for fabrication inspection requirements. Other inspection requirements are in Section 16. | Design review of lifting points Detailed lift plan and review with vessel operators | All lift points reviewed per specifications | 2020-04-15 | Closed | 5 | 2 | Med | 10 | 9.6
|  | X.0410.2 | Lifting device with crane | Use either vessel crane or pier crane to transfer device from pier to installation vessel | 1 | None (device will have been previously lifted during transportation) | Lifting equipment failure | Large angle on slings Inadequate lift plan Lifting equipment not properly inspected | Visual inspection | Personel injury Damage to WEC | SOP to inspect all lifting equipment periodically and prior to use | 5 | 2 | Med | 10 | All lift points, rigging etc. should be designed, manufactured and inspected according to DNVGL-ST-N001 See Table 5-11 for fabrication inspection requirements. Other inspection requirements are in Section 16. | Design review of lifting points Detailed lift plan and review with vessel operators | Third Party (Crane company) review of lifting procedure and riging equipment. CalWave to review DNVGL-ST_N001 and confirm appropriate implementation. | 2020-08-30 | Closed | 5 | 2 | Med | 10 | 9.6
|  | X.0410.3 | Lifting device with crane | Use either vessel crane or pier crane to transfer device from pier to installation vessel | 1 | None (device will have been previously lifted during transportation) | Insufficient or inappropriatly placed lifting eyes | Insufficient lift plan incorporated into hull design | Visual inspection | Personel injury Damage to WEC | Incorporate transportation logistics into hull design SOP to inspect all lifting equipment periodically and prior to use | 4 | 2 | Med | 8 | All lift points, rigging etc. should be designed, manufactured and inspected according to DNVGL-ST-N001 See Table 5-11 for fabrication inspection requirements. Other inspection requirements are in Section 16. | Design review of lifting points Detailed lift plan and review with vessel operators | All lift points reviewed per specifications | 2019-10-31 | Closed | 4 | 2 | Med | 8 | 9.6
|  | X.0410.4 | Lifting device with crane | Use either vessel crane or pier crane to transfer device from pier to installation vessel | 1 | None (device will have been previously lifted during transportation) | Load exceedence of vessel crane | Incorrect weight estimates of WEC | CAD review Lift test | Personel injury Damage to WEC Damage to crane | Thorough CAD review of complete assembed weight Lift test to experimentially determine weight if possible Review lift plan with vessel operator | 4 | 2 | Med | 8 | All lift points, rigging etc. should be designed, manufactured and inspected according to DNVGL-ST-N001 See Table 5-11 for fabrication inspection requirements. Other inspection requirements are in Section 16. | Design review of lifting points Detailed lift plan and review with vessel operators | Complete component weight breakdown included in device CAD. Components are weighted prior to assembly to confirm total weight. | 2020-08-30 | Closed | 4 | 2 | Med | 8 | 9.6
|  | X.0410.5 | Lifting device with crane | Use either vessel crane or pier crane to transfer device from pier to installation vessel | 1 | None (device will have been previously lifted during transportation) | Weather constraints | Using vessel crane likely has more restrictive weather limits for lifting | Weather monitoring | Personel injury Damage to WEC Damage to crane | Review lift plan with vessel operator | 3 | 2 | Low | 6 | Use tag lines to control motion while suspended if necessary |  |  | N/A | Closed | 3 | 2 | Low | 6 | 9.6
| X.0500 |  | Towing device to site | [16 empty] | open
|  | X.0510.1 | Tow device with vessel | Verify tow line configuration and device response, verify towing speeds and line handling procedures | 2 | Device geometry | Contact with seafloor during tow | Towing during low tide and/or at shallow harbor | Tow plan | Damage to WEC | Consider harbor depth and tide in tow plan | 3 | 2 | Low | 6 |  |  | Performed Ocraflex dynamic modelling of various sea states | 05/15/2020 | Closed | 3 | 2 | Low | 6 | 9.6
|  | X.0510.2 | Tow device with vessel | Verify tow line configuration and device response, verify towing speeds and line handling procedures | 2 | Device geometry | Vessel traffic during tow | Towing during busy period or from busy port | Tow plan | Delays Increased risk for contact with vessel | Consider in tow plan | 2 | 3 | Low | 6 | Consider if guard vessel is appropriate. |  | Performed Ocraflex dynamic modelling of various sea states | 05/15/2020 | Closed | 2 | 3 | Low | 6 | 9.6
|  | X.0510.3 | Tow device with vessel | Verify tow line configuration and device response, verify towing speeds and line handling procedures | 2 | Device geometry | Contact with tow vessel | Insufficient tow line distance or arrangement Wave loads during tow Abrupt vessel movement | Tow plan | Damage to WEC Damage to vessel | Review tow plan with vessel operators Consider alongside tow to reduce risk | 4 | 2 | Med | 8 |  | Design review of tow plan Detailed tow plan and review with vessel operators | Tow plan and towing hardware reviewed with local operations partners. Towing load estimates calculated with partners. | 3/15/2020 | Closed | 3 | 2 | Low | 6 | 9.6
|  | X.0510.4 | Tow device with vessel | Verify tow line configuration and device response, verify towing speeds and line handling procedures | 2 | Device geometry | Slack/snap load on towing line | Insufficient tow line distance or arrangement Wave loads during tow Abrupt vessel movement | Tow plan | Damage to WEC at connection point Damage to vessel | Review tow plan with vessel operators Consider alongside tow to reduce risk | 4 | 2 | Med | 8 |  | Design review of tow plan Detailed tow plan and review with vessel operators | Tow plan and towing hardware reviewed with local operations partners. Towing load estimates calculated with partners. | 3/15/2020 | Closed | 3 | 2 | Low | 6 | 9.6
|  | X.0510.5 | Tow device with vessel | Verify tow line configuration and device response, verify towing speeds and line handling procedures | 2 | Device geometry | Crack/structural failure | Fatigue during towing | Tow plan | Damage to WEC at connection point Damage to vessel | Review tow plan with vessel operators Consider alongside tow to reduce risk | 5 | 3 | High | 15 |  | Fatigue assessement | Tow plan and towing hardware reviewed with local operations partners. Towing load estimates calculated with partners. | 3/15/2020 | Closed | 5 | 2 | Med | 10 | 9.6
|  | X.0510.6 | Tow device with vessel | Verify tow line configuration and device response, verify towing speeds and line handling procedures | 2 | Device geometry | Overturning | Instability during tow | Visual observation | Damage to WEC at connection point Damage to vessel | Review tow plan with vessel operators Consider alongside tow to reduce risk | 5 | 3 | High | 15 |  | Perform metastatic analysis for structure under tow | Perform metacentric height analysis for floating device | 5/15/2020 | Open | 5 | 2 | Med | 10 | 9.6
|  | X.0511.1 | Monitor during towing | Ensure tow line loads and device watertight integrity during tow operations | 2 | Novel device | Instability during tow | Unanticipated loads during tow | Tow winch load cell | Damage to WEC Increased load on tow lines | Adequate leak test of hull prior to towing Use winch load cell to monitor tow line loads Review tow plan with vessel operators Consider alongside tow to reduce risk | 3 | 3 | Med | 9 |  | Design review of tow plan Detailed tow plan and review with vessel operators | Tow plan and towing hardware reviewed with local operations partners. Towing load estimates calculated with partners. | 3/15/2020 | Closed | 3 | 2 | Low | 6 | 9.6
|  | X.0511.2 | Monitor during towing | Ensure tow line loads and device watertight integrity during tow operations | 2 | Novel device | Seawater ingress during tow | Structural/seal failure during tow Unanticipated loads during tow Blowout valve failure during tow | Tow winch load cell | Increased loads on tow lines Loss of WEC | Adequate leak test of hull prior to towing Use winch load cell to monitor tow line loads Review tow plan with vessel operators Consider alongside tow to reduce risk | 5 | 2 | Med | 10 |  | Design review of tow plan Detailed tow plan and review with vessel operators | Tow plan and towing hardware reviewed with local operations partners. Towing load estimates calculated with partners. | 3/15/2020 | Closed | 5 | 2 | Med | 10 | 9.6
| X.0600 |  | Connecting mooring lines to PTO belt | [16 empty] | open
|  | X.0610.1 | Retrieve mooring line from bridal | With device alongside vessel, use tender (RIB) to retrive first mooring line and bring to connection point | 1 | Connection procedures still to be established | Mooring line disconnects from bridal | Inadequatly secured hardware Excessive weather with moorings in place, prior to connecting to WEC (no tension on moorings) Human error (dropped hardware) Working from small vessel | Visual inspection | Delay Potential damage to mooring line | Detailed and reviewed installation plan Qualified personnel for working offshore | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 9.6
|  | X.0610.2 | Retrieve mooring line from bridal | With device alongside vessel, use tender (RIB) to retrive first mooring line and bring to connection point | 1 | Connection procedures still to be established | Personnel safety working offshore | Pinch points between vessel and buoy Potential for man overboard Slips, trips, falls | Safety SOP | Human safety | Safety SOP Only qualified personnel working offshore | 5 | 2 | Med | 10 |  | Develop health & safety procedures Perform HAZID with local operators prior to any operations | HSE plan in place Operations plans reviewed with offshore partners. HAZID will be performed with local operators shortly before operations. | 8/15/2020 | Closed | 5 | 1 | Med | 5 | 9.6
|  | X.0620.1 | Connect mooring line to winch belt | For demo scale, connect from RIB with standard shackle or similiar | 2 | Connection procedures still to be established - vessel requirements and connection hardware for full scale to be determined | Mooring line disconnects from bridal | Inadequatly secured hardware Excessive weather with moorings in place, prior to connecting to WEC (no tension on moorings) Human error (dropped hardware) Working from small vessel | Visual inspection | Delay Potential damage to mooring line | Detailed and reviewed installation plan Qualified personnel for working offshore | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 9.6
|  | X.0620.2 | Connect mooring line to winch belt | For demo scale, connect from RIB with standard shackle or similiar | 2 | Connection procedures still to be established - vessel requirements and connection hardware for full scale to be determined | Personnel safety working offshore | Pinch points between vessel and WEC Potential for man overboard Slips, trips, falls | Safety SOP | Human safety | Safety SOP Only qualified personnel working offshore | 5 | 3 | High | 15 |  | Develop health & safety procedures Perform HAZID with local operators prior to any operations | HSE plan in place Operations plans reviewed with offshore partners. HAZID will be performed with local operators shortly before operations. | 8/15/2020 | Closed | 5 | 2 | Med | 10 | 9.6
|  | X.0620.3 | Connect mooring line to winch belt | For demo scale, connect from RIB with standard shackle or similiar | 2 | Connection procedures still to be established - vessel requirements and connection hardware for full scale to be determined | Vessel contact with WEC | Inadequate design or plan for connection Wave/wind loads during operation Abrupt vessel movement | Installation plan | Damage to WEC Damage to vessel | Review installation plan with vessel operators Place vessel on windward side of WEC to reduce wind/wave loads on WEC | 4 | 2 | Med | 8 |  | Iterate operations plans with local vessel operators | Operations plans reviewed with offshore partners. HAZID will be performed with local operators shortly before operations. | 8/15/2020 | Closed | 4 | 1 | Low | 4 | 9.6
|  | X.0630.1 | Bring mooring lines into tension to ensure station keeping prior to vessel moving to observation position | Use device controls to bring mooring lines into tension | 2 | Device controls | Winch fails to operate | Communication fault Hardware fault | SCADA | Inability to deploy - cost & program delay Additional load on mooring lines/damage to mooring system | PTO test bench Verify anchor placement Test winch ashore prior to deployment | 4 | 2 | Med | 8 |  | Perform HAZID with local operators prior to any operations Contingence plan to be developed for winch failure. | Operations plans reviewed with offshore partners. HAZID will be performed with local operators shortly before operations. | 8/15/2020 | Closed | 4 | 2 | Med | 8 | 9.6
|  | X.0630.2 | Bring mooring lines into tension to ensure station keeping prior to vessel moving to observation position | Use device controls to bring mooring lines into tension | 2 | Device controls | WEC fails to submerge | Insufficent motor capacity Loads higher than anticipated | Visual inspection | Inability to deploy - cost & program delay | PTO test bench Verify anchor placement Test winch ashore prior to deployment | 3 | 3 | Med | 9 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 9.6
|  | X.0630.3 | Bring mooring lines into tension to ensure station keeping prior to vessel moving to observation position | Use device controls to bring mooring lines into tension | 2 | Device controls | WEC fails to submerge in even, stable configuration (unintented pitch angle) | Communication fault Motor operation and/or loads uneven (anchor spacing not even) | Visual inspection | Inability to deploy - cost & program delay | PTO test bench Verify anchor placement Test winch ashore prior to deployment | 3 | 3 | Med | 9 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 9.6
|  | X.0630.4 | Bring mooring lines into tension to ensure station keeping prior to vessel moving to observation position | Use device controls to bring mooring lines into tension | 2 | Device controls | Communication failure once WEC is submerged | Communication path unreliable when submerged | SCADA | Inability to deploy - cost & program delay | Redundant methods of communication Adequatly test all communication methods | 3 | 3 | Med | 9 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 9.6
| X.0700 |  | Connecting umbillical to device | [16 empty] | open
|  | X.0710.1 | Retrieve umbilical | Pickup umbilical for connection | 2 | Strain termination & connection to WEC | Pickup buoy off station | Hardware failure Human error (not securring pin, etc) | Visual inspection | Cost and program delay (required dive operation to retrieve) | Review operational planning vessel operators | 3 | 1 | Low | 3 | Consideration of marine vessel traffic should be taken into account when planning operation |  |  | N/A | Closed | 3 | 1 | Low | 3 | 9.6
|  | X.0710.2 | Retrieve umbilical | Pickup umbilical for connection | 2 | Strain termination & connection to WEC | Damage to umbilical during operation | Abraision Contact with vessel or subsea equipment | Drop camera | Cost and program delay | Review operational planning vessel operators Use cable protection where appropriate | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 9.6
|  | X.0710.3 | Retrieve umbilical | Pickup umbilical for connection | 2 | Strain termination & connection to WEC | Exceed minimum bend radius during operation | Lay plan does not adequatly consider lay angles Vessel does not adequatly follow lay plan | Vessel GPS Drop camera | Damage to umbilical | Review operational planning with vessel operators Use cable protection where appropriate | 3 | 2 | Low | 6 | Installation analyses should be performed using conservative assumptions. Section 7 of DNVGL-ST-N001, ref. /8/ contains details on installation requirements and analyses. |  |  | N/A | Closed | 3 | 2 | Low | 6 | 9.6
|  | X.0710.4 | Retrieve umbilical | Pickup umbilical for connection | 2 | Strain termination & connection to WEC | Damage to vessel | Umbilical comes up into propeller | Drop camera | Cost and program delay | Plan for drop camera use during operation Review operational planning with vessel operators | 4 | 2 | Med | 8 |  | Detailed install procedures Perform HAZID with local operators prior to any operations | Operations plans reviewed with offshore partners. HAZID will be performed with local operators shortly before operations. | 8/15/2020 | Closed | 3 | 2 | Low | 6 | 9.6
|  | X.0710.5 | Retrieve umbilical | Pickup umbilical for connection | 2 | Strain termination & connection to WEC | Entaglement with other subsea infrastructure and/or lines | Insufficient touchdown anchor Excessive wave loading Unanticipated subsea dynamics | Drop camera | Damage to umbilical Damage to other subsea infrastructure | Seafloor survey prior to cable lay Plan for drop camera use during operation Review operational planning with vessel operators | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 9.6
|  | X.0720.1 | Electrical testing prior to connection | Verify continuity and insulation resistance of umbilical prior to connection (dependant upon communications or other sensitive equipment) | 2 | Novel design electrical system will need to be considered as to what can be tested prior to connection | Damage to communications equipment or other sensitive electronics | Insulation resistance testing inducing current in communications or other sensitive electronics | SCADA | Repair needed on WEC Cost and program delay | Electrical testing SOP Electrical safety SOP | 3 | 2 | Low | 6 | SOP to identify qualified personnel to perform electrical connections |  |  | N/A | Closed | 3 | 2 | Low | 6 | 9.6
|  | X.0720.2 | Electrical testing prior to connection | Verify continuity and insulation resistance of umbilical prior to connection (dependant upon communications or other sensitive equipment) | 2 | Novel design electrical system will need to be considered as to what can be tested prior to connection | Electric shock | Improper electrical safety Inadequate short circuit protection | Safety observer | Human safety | Electrical testing SOP Electrical safety SOP | 5 | 2 | Med | 10 | SOP to identify qualified personnel to perform electrical connections | Develop electrical safety procedures Perform HAZID with local operators prior to any operations | HSE plan in place Electrical connection operations reviewed with offshore partners, will be reviewed again during pre-operation HAZID | 5/15/2020 | Closed | 5 | 2 | Med | 10 | 9.6
|  | X.0730.1 | Make electrical connection | Connect umbilical to device using standard splash zone connector | 1 | Test procedure to ensure proper operation post connection, prior to vessel moving off station | Electric shock | Improper electrical safety Improper wiring | Safety observer | Human safety | Electrical testing SOP Electrical safety SOP | 5 | 2 | Med | 10 | SOP to identify qualified personnel to perform electrical connections | Develop electrical safety procedures Perform HAZID with local operators prior to any operations | HSE plan in place Electrical connection operations reviewed with offshore partners, will be reviewed again during pre-operation HAZID | 5/15/2020 | Closed | 5 | 2 | Med | 10 | 9.6
|  | X.0730.2 | Make electrical connection | Connect umbilical to device using standard splash zone connector | 1 | Test procedure to ensure proper operation post connection, prior to vessel moving off station | Damage to electrical equipment | Short circuit Incorrect electrical system changes since previous connection | SCADA | Repair needed on WEC Cost and program delay | Electrical testing SOP Electrical safety SOP | 3 | 2 | Low | 6 | SOP to identify qualified personnel to perform electrical connections |  |  | N/A | Closed | 3 | 2 | Low | 6 | 9.6
| X.0800 |  | Adjusting device to operating location | [16 empty] | open
|  | X.0810.1 | Submerge device from surface | Adjust device from surface to submerged posture | 4 | Novel operational procedures | Instability as WEC transitions to submerged position | Hardware failure Controls/software/communication failure Uneven PTO operation | Visual Winch position | Delays, inability to stay deployed Risk of WEC damage if not in correct position | PTO bench testing | 4 | 2 | Med | 8 |  | Detailed install procedures Perform HAZID with local operators prior to any operations | Operations plans reviewed with offshore partners. HAZID will be performed with local operators shortly before operations. | 8/15/2020 | Closed | 4 | 2 | Med | 8 | 9.6
|  | X.0810.2 | Submerge device from surface | Adjust device from surface to submerged posture | 4 | Novel operational procedures | Slamming loads on hull prior to submergence | Higher than expected sea state Longer than anticipated to lower Inadequate hull structural analysis | Visual | Failure of hull Seawater ingress | Plan for vessel to be on windward side of WEC during install Review operational planning with vessel operators Operations SOP | 4 | 2 | Med | 8 |  | Detailed install procedures Perform HAZID with local operators prior to any operations | Operations plans reviewed with offshore partners. HAZID will be performed with local operators shortly before operations. | 8/15/2020 | Closed | 4 | 2 | Med | 8 | 9.6
|  | X.0810.3 | Submerge device from surface | Adjust device from surface to submerged posture | 4 | Novel operational procedures | Seawater ingress | Enclosure not properly closed and sealed Seal failure | Water detectors | Failure of electrical equipment Loss of WEC | Plan for vessel to be on windward side of WEC during install Review operational planning with vessel operators Operations SOP | 4 | 2 | Med | 8 |  | Detailed install procedures Perform HAZID with local operators prior to any operations | Operations plans reviewed with offshore partners. HAZID will be performed with local operators shortly before operations. | 8/15/2020 | Closed | 4 | 2 | Med | 8 | 9.6
|  | X.0810.4 | Submerge device from surface | Adjust device from surface to submerged posture | 4 | Novel operational procedures | Inability to maintain correct depth | Controls failure Hardware failure | Winch position Mooring tension | Increased potential for damage to WEC Program delays Inability to obtain test data | PTO bench testing | 4 | 2 | Med | 8 |  | Detailed install procedures Perform HAZID with local operators prior to any operations | Operations plans reviewed with offshore partners. HAZID will be performed with local operators shortly before operations. | 8/15/2020 | Closed | 4 | 2 | Med | 8 | 9.6
|  | X.0820.1 | Adjust between submerged depths | Adjust device from surface to submerged posture | 4 | Novel operational procedures | Inadequate power to perform operation | Transition from low sea state without power generation and insufficient onboard battery storage | Motor current Winch position Mooring tension | Inability to move to operational depth WEC in exposed position if higher sea states occur | Size onboard storage with adequate safety margin | 3 | 2 | Low | 6 | Trade off on size/weight of battery backup and operational limitations | In depth analysis on required capacity |  | N/A | Closed | 3 | 2 | Low | 6 | 9.6
|  | X.0820.2 | Adjust between submerged depths | Adjust device from surface to submerged posture | 4 | Novel operational procedures | Incorrect pretension in system | Controls failure Sensor failure | Mooring tension | WEC in exposed position resulting in potentially higher than anticipated loads or lower than anticipated performance | Redundant sensors, manual cross check between PTOs | 4 | 3 | Med | 12 | Review options for redundant sensors | Automated flag in SCADA for normalized PTO mismatch |  | N/A | Closed | 4 | 2 | Med | 8 | 9.6
|  | X.0830.1 | Establish gas spring position/pressure | Establish and maintain correct gas spring & accumulator pressure and stroke position | 4 | Novel operational procedures | Incorrect gas spring stroke position | Controls failure Sensor failure | Position sensor Pressure sensor | WEC in exposed position resulting in potentially higher than anticipated loads or lower than anticipated performance | PTO bench testing | 4 | 3 | Med | 12 |  |  |  | N/A | Closed | 4 | 2 | Med | 8 | 9.6
|  | X.0830.2 | Establish gas spring position/pressure | Establish and maintain correct gas spring & accumulator pressure and stroke position | 4 | Novel operational procedures | Incorrect gas spring pressure | Accumulator not maintaining pressure Hydraulic leak Communications/software fault Controls fault | Pressure sensor Position sensor | WEC in exposed position resulting in potentially higher than anticipated loads or lower than anticipated performance | PTO bench testing | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 9.6
|  | X.0830.3 | Establish gas spring position/pressure | Establish and maintain correct gas spring & accumulator pressure and stroke position | 4 | Novel operational procedures | Incorrect gas spring pressure | Hardware failure Controls failure | Pressure sensor Position sensor | WEC in exposed position resulting in potentially higher than anticipated loads or lower than anticipated performance | PTO bench testing | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 9.6
| X.0900 |  | Operating device with full perforrmance | [16 empty] | open
|  | X.0910.1 | Operating device with basic functionality | Upon initial deployment, verify device functionality and safety of operation. Beyond actions covered in 0800 this would include items such as power generation and dissipation, data logging and analysis, communication, etc., | 3 | Novel operational procedures | Extreme weather - above design considerations and/or arising quickly | The Ultimate Limit States that defines the design basis requirements is dependent on the definition of the extreme sea state. | Mooring loads | Loads higher than designed for occuring prior to ability to transition WEC to survival state | Compliance with the IEC TS 62600-103 and other relevant standards and application of higher safety factor for this demonstration project is used. | 4 | 3 | Med | 12 | Ensure insurance policy adequately covers expected losses; have staff attorney review policy; | Ensure adequate design sea state taken into design considerations | Statistical design tools for 50-year sea state were used. Sensitivity analysis conducted (Toan) CFD focused wave approach used for survival loads | 05/01/2019 | Closed | 4 | 2 | Med | 8 | 10.1
|  | X.0911.1 | Communication functionality | Validate all forms of communication, including failover procedure, sending commands and recieving feedback while submerged from all forms of communication | 3 | Novel operational procedures | Loss of communication during operation | Power cycle to communications equipment Service interruption | SCADA Watchdog timer | Loss of situational awareness Loss of operator input ability | PTO bench testing Startup BIT | 3 | 3 | Med | 9 |  | SCADA testing during PTO bench test Pre-deployment checkout testing Auto-reboot routines and watchdog timers on the SCADA/PLC Hardware/SCADA to manually connect when close to device (WLAN) | Operations plans reviewed with offshore partners. HAZID will be performed with local operators shortly before operations. | 8/15/2020 | Closed | 3 | 2 | Low | 6 | 10.1
|  | X.0912.1 | Software functionality | Validate software functionality while submerged | 3 | Novel operational procedures | Software failure during operation | Power cycle Cable disconnection or failure Failed built in test (BIT) | Software BIT | WEC shutdown Loss of situational awareness Loss of operator input ability | PTO bench testing Startup BIT | 3 | 3 | Med | 9 |  | SCADA testing during PTO bench test Pre-deployment checkout testing Auto-reboot routines and watchdog timers on the SCADA/PLC | Operations plans reviewed with offshore partners. HAZID will be performed with local operators shortly before operations. | 8/15/2020 | Closed | 3 | 2 | Low | 6 | 10.1
|  | X.0912.2 | Software functionality - control loop | Validate software functionality while submerged | 3 | Novel operational procedures | Uneven PTO operation or unexpected PTO operation | Latency in control software | Visual Winch position | Delays, inability to stay deployed Risk of WEC damage if not in correct position | PTO bench testing | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 10.1
|  | X.0913.1 | Power system functionality | Validate power system functionality while submerged | 3 | Novel operational procedures | Excessive heat generated in braking resistors | Discrepency in generated/dissipated heat, compared to expected | Climate control data | WEC shutdown Loss of situational awareness Loss of operator input ability | PTO bench testing Oversized braking resistors | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 10.1
|  | X.0914.1 | Hydraulic system functionality | Validate hydraulic system functionality while submerged | 3 | Novel operational procedures | Hydraulic leaks | Loose valve or fixture | Hydraulic pressure | Increased chance of gas spring end stop impact WEC operating outside of optimial conditions | PTO bench testing Hydraulics pressure/leak checks prior to deployment | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 10.1
|  | X.0914.2 | Hydraulic system functionality | Validate hydraulic system functionality while submerged | 3 | Novel operational procedures | Hydraulic temperature higher than expected | Heat generated in friction losses (seals, turns, piping, etc.,) | Hydraulic temperature | Increased risk of hydraulic system failure | PTO bench testing | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 10.1
|  | X.0914.3 | Hydraulic system functionality | Validate hydraulic system functionality while submerged | 3 | Novel operational procedures | Hydraulic presure higher than expected | Controls fault | Hydraulic pressure | Increased risk of hydraulic system failure | PTO bench testing | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 10.1
|  | X.0915.3 | Auxiliary systems functionality | Validate functionality of all auxiliary systems while submerged | 3 | Novel operational procedures | Holding system capacity full with continued seawater ingress | Seawater ingress (significant) | Ballast tank level Bilge pump run time | Inability to remove fluid from enclosures | Inherent control in that increasing ballast system volume will increase WEC depth which will place WEC in safest operational posture Emergency operating procedures | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 10.1
|  | X.0915.4 | Auxiliary systems functionality | Validate functionality of all auxiliary systems while submerged | 3 | Novel operational procedures | Cooling failure to generator | Loss of power to cooling system Generator creating more heat than expected Air cooling works less efficiently than expected | Cooling fan run time | Increased temperature in generator Potential for generator shutdown | PTO bench testing to characterize generator heat generation Oversized generator Appropriate safety factor on forced cooling solution | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 10.1
|  | X.0915.5 | Auxiliary systems functionality | Validate functionality of all auxiliary systems while submerged | 3 | Novel operational procedures | Fire detection/suppression accidential discharge | Mechanical failure | SCADA | Damage to electrical equipment Loss of fire suppression system | Safety of system design Select safe materials for fire suppression | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 10.1
|  | X.0915.6 | Auxiliary systems functionality | Validate functionality of all auxiliary systems while submerged | 3 | Novel operational procedures | Loss of power to humitidy control system | Total loss of power Cable disconnection or failure | Humidity sensor | Loss of ability to control humidity Potential for ncreased condensation Potential to damage electrical components | Reviewing options for humitidy control, including passive options (e.g. dessicant packs) | 4 | 3 | Med | 12 |  | Calculate humidity control requirements and validate implimentation | Calculations show active humidity control not required | 2019-10-15 | Closed | 4 | 2 | Med | 8 | 10.1
|  | X.0915.7 | Auxiliary systems functionality | Validate functionality of all auxiliary systems while submerged | 3 | Novel operational procedures | Accumulation of condensation greater than expected | Higher humitidy than anticipated Lack of air exchange in submerged enviornment | Bilge pump run time | Increased run time on bilge pumps Potential to fill ballast tanks Potential to damage electrical components |  | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 10.1
|  | X.0915.8 | Auxiliary systems functionality | Validate functionality of all auxiliary systems while submerged | 3 | Novel operational procedures | Humidity higher than expected | Higher heat in enclosure than expected Lack of air exchange in submerged enviornment | Humidity sensor Bilge pump run time | Increased condensation Potential to damage electrical components |  | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 10.1
|  | X.0915.9 | Submerge device control | Validate functionality of all auxiliary systems while submerged | 3 | Novel operational procedures | Submergence depth not ensured | Higher load on PTO then desgined for. Lack of air exchange in submerged enviornment | Humidity sensor Bilge pump run time | Increased condensation Potential to damage electrical components |  | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 10.1
|  | X.0920.2 | Validating full functionality and performance data retrival and analysis | Demonstrate tuning of parameters and ability to analyze collected data to correlate parameter tuning to performance | 4 | Novel operational procedures | Corrupt data | Software failure Time syncronization failure | Data logging Watchdog timer | Lost test time |  | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 10.1
|  | X.0920.2 | Validating full functionality and performance data retrival and analysis | Demonstrate tuning of parameters and ability to analyze collected data to correlate parameter tuning to performance | 4 | Novel operational procedures | inability to access data while deployed | Communications failiure | Data logging | Loss of situational awareness Loss of informed operator input ability |  | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 10.1
|  | X.0930.1 | Operating with optimized performance | Obtain and maintain optimized parameter setting to collect and analyze data in target sea states | 3 | Novel operational procedures | Reduced power production compared to expectations | Inaccurate modelling WEC build not as designed | Performance metrics | Partial loss of credibility Increased difficulty/delay in continued funding | Adequate sensors and post processing to characterize losses in both mechanical and electrical conversion chain to determine if adjustments in control strategy or physical device is possible within test window | 4 | 2 | Med | 8 |  | Performance characterization during PTO testing Post processing for performance early in testing Fabrication contractor oversight Numerical Model update from given hardware once WEC is build | Derived physical properties of actual hardware build/going to be deployed to update simulations/expectations. | 08/01/2020 | Closed | 4 | 2 | Med | 8 | 10.1
|  | X.0930.2 | Operating with optimized performance | Obtain and maintain optimized parameter setting to collect and analyze data in target sea states | 3 | Novel operational procedures | Low availability | Component reliability issues Communication issues Lack of weather windows for maintenance | Data logging | Partial loss of credibility Increased difficulty in aquiring sufficient test data | PTO test bench Investigating opportunities for parallel reliability lab testing | 3 | 3 | Med | 9 |  | Sensor checkout and data post processing during PTO test bench testing Reliable physical designs with sufficient safety factors to ensure availability of all subcomponents. | Sensors initialized and validated in PTO bench testing | 08/15/2020 | Closed | 3 | 2 | Low | 6 | 10.1
|  | X.0931.1 | Data post processing | Optimize post processing scripts for data analysis | 3 | Novel operational procedures | Incomplete data collection during test campaign | Sensor failure Insufficient sensors | Data logging | Partial loss of credibility Increased difficulty in aquiring sufficient test data | PTO test bench Redundancy & reliability of sensors | 3 | 3 | Med | 9 |  | Deploy in spring to gather data from ideal scale sea states in summer PTO bench testing | Sensor bandwidth and suitability verified on bench. Post processing routines similar to wave tank testing and numerical modeling post processing routines. | 08/15/2020 | Closed | 3 | 2 | Low | 6 | 10.1
|  | X.0931.2 | Data post processing | Optimize post processing scripts for data analysis | 3 | Novel operational procedures | Insufficient data collection during test campaign | Low availability of WEC Insufficient weather to test necessary sea states | Data logging | Partial loss of credibility Increased difficulty in aquiring sufficient test data | PTO test bench Investigating opportunities for parallel reliability lab testing | 3 | 3 | Med | 9 |  | Deploy in spring to gather data from ideal scale sea states in summer PTO bench testing Sensor redundancy Post processing routines developed in coherence with SCADA development | Sensors initialized and validated in PTO bench testing Numerical model capabilities to replicate sea states of interest from device behavior in sea states of lesser interest | 08/15/2020 | Closed | 3 | 2 | Low | 6 | 10.1
| X.1000 |  | Changing operating depth | [16 empty] | open
|  | X.1010 | Same procedure as 0820 | [21 empty] | 10.5
| X.1100 |  | Tidal adjustment | [16 empty] | open
|  | X.1110.1 | Adjust PTO/moorings to accomidate tidal variations | In order to adjust for tide while maintaining the gas spring operating in the center of stroke, an approx once daily operation will need to occur whereby the shaft clutch is disengaged and the winch drum operated independant of the gas spring, and the clutch recoupled | 4 | Novel operational procedures | Failure of clutch/brake mechanism | Clutch fails to engage/disengage as required Brake fails to engage/disengage as required Uneven PTO operation | Shaft torque Hydraulic pressure | Inability to perform depth change Inability to recover from depth change Shock loads on system | PTO test bench Failsafe design for clutch and brake | 4 | 2 | Med | 8 |  | Bench test depth change operations | Clutch and brake removed from design. CONFIRM HPU FAILURE IS ACCOUNTED FOR ELSEWHERE. | 2019-08-26 | Closed | 4 | 2 | Med | 8 | 10.4
| X.1200 |  | Transition to/from survival mode | [16 empty] | open
|  | X.1220.1 | Recover device from emergency survival mode position | Manual operation requiring divers | 3 | Novel operational procedures | Inability to remove water from ballast system | Corroded or otherwise inaccessible connection point WEC movement beyond safe limits for diver approach | Visual inspection | Need to cut mooring line or recover anchor under load in order to retrieve WEC | Pump out system and access designed for diver access | 5 | 3 | High | 15 |  | Investigate a passive ballast system | Updated design with passive ballast system that maintains positive buoyancy with entrapment chambers full | 2019-01-01 | Closed | 4 | 2 | Med | 8 | 10.4
| X.1300 |  | Bringing device to surface for maintenance | [16 empty] | open
|  | X.1310.1 | Controlled release of PTO winch to bring device to surface | Use motor/generator set to increase mooring line length until device is accessible on surface, but still under tension to be stable | 3 | Novel operational procedures | Winch system failure | Siezed shaft Seperated belt | SCADA Drop camera | Additional time/cost in recovery | Design belt length for three PTOs to recover to surface in event of failed PTO/winch | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 10.4
|  | X.1320.1 | Access hatch from vessel | Determine requirements for access hatch that can be accessed from a vessel without compromising watertight integrity (software, electrical, hydraulics) | 3 | Novel operational procedures | WEC not stable at surface | Unanticipated WEC motion while in transition state | Visible from vessel | Human safety Vessel safety | Compliance with the IEC TS 62600-103 and other relevant standards and application of higher safety factor for this demonstration project is used. | 3 | 2 | Low | 6 | Determine safest possible approach and SOP for interaction with access hatch | Develop SOP for access hatch |  | N/A | Closed | 3 | 2 | Low | 6 | 10.4
|  | X.1330.1 | Transfer personnel for maintenance | Safely allow for personnel to transfer to top of device and access maintenance ports | 2 | Novel operational procedures | WEC not stable at surface | Unanticipated WEC motion while in transition state | Visible from vessel | Human safety Vessel safety | Compliance with the IEC TS 62600-103 and other relevant standards and application of higher safety factor for this demonstration project is used. | 5 | 3 | High | 15 | Determine if transferring personnel to WEC at sea is critically needed | Develop SOP, include possiblity for rails or other safety equipment | Performing service inside WEC at sea determined not to be feasible at this scale | 2019-01-01 | Closed | 4 | 1 | Low | 4 | 10.4
|  | X.1331.1 | Tie up vessel to device & personnel transfer | Ensure appropriate chocks or other accessible tie up points and establish operational procedures for personnel transfer (may need handrails?) | 2 | Novel operational procedures | WEC not stable at surface | Unanticipated WEC motion while in transition state | Visible from vessel | Human safety Vessel safety | Compliance with the IEC TS 62600-103 and other relevant standards and application of higher safety factor for this demonstration project is used. | 5 | 3 | High | 15 | Determine if transferring personnel to WEC at sea is critically needed | Develop SOP, include possiblity for rails or other safety equipment | Performing service inside WEC at sea determined not to be feasible at this scale | 2019-01-01 | Closed | 4 | 1 | Low | 4 | 10.4
|  | X.1332.1 | Perform PTO service via PTO access hatch | Ensure appropriate weather window and safety of equipment from seawater ingress, ensure watertight integrity is maintained by reconstituting watertight seals | 3 | Novel operational procedures | WEC not stable at surface | Unanticipated WEC motion while in transition state | Visible from vessel | Human safety Vessel safety | Compliance with the IEC TS 62600-103 and other relevant standards and application of higher safety factor for this demonstration project is used. | 5 | 3 | High | 15 | Determine if transferring personnel to WEC at sea is critically needed | Develop SOP, include possiblity for rails or other safety equipment | Performing service inside WEC at sea determined not to be feasible at this scale | 2019-01-01 | Closed | 4 | 1 | Low | 4 | 10.4
|  | X.1333.1 | Perform hydraulic service via hydraulic system access hatch | Ensure appropriate weather window and safety of equipment from seawater ingress, ensure watertight integrity is maintained by reconstituting watertight seals | 3 | Novel operational procedures | WEC not stable at surface | Unanticipated WEC motion while in transition state | Visible from vessel | Human safety Vessel safety | Compliance with the IEC TS 62600-103 and other relevant standards and application of higher safety factor for this demonstration project is used. | 4 | 3 | Med | 12 | Determine if transferring personnel to WEC at sea is critically needed | Develop SOP, include possiblity for rails or other safety equipment | Evolve specifications and operations planning for operator interfacing with access hatch at sea (from support vessel) | 11/01/2020 | Open | 3 | 2 | Low | 6 | 10.4
|  | X.1334.1 | Perform electrical/power system service via electrical service hatch (including communication and software) | Ensure appropriate weather window and safety of equipment from seawater ingress, ensure watertight integrity is maintained by reconstituting watertight seals | 3 | Novel operational procedures | WEC not stable at surface | Unanticipated WEC motion while in transition state | Visible from vessel | Human safety Vessel safety | Compliance with the IEC TS 62600-103 and other relevant standards and application of higher safety factor for this demonstration project is used. | 4 | 3 | Med | 12 | Determine if transferring personnel to WEC at sea is critically needed | Develop SOP, include possiblity for rails or other safety equipment | Evolve specifications and operations planning for operator interfacing with access hatch at sea (from support vessel) | 11/01/2020 | Open | 3 | 2 | Low | 6 | 10.4
|  | X.1334.2 | Perform electrical/power system service via electrical service hatch (including communication and software) | Ensure appropriate weather window and safety of equipment from seawater ingress, ensure watertight integrity is maintained by reconstituting watertight seals | 3 | Novel operational procedures | Electric shock | Improper electrical safety Improper wiring | Safety observer | Human safety | Electrical testing SOP Electrical safety SOP | 5 | 2 | Med | 10 | Determine if transferring personnel to WEC at sea is critically needed | Develop SOP, include possiblity for rails or other safety equipment | Evolve specifications and operations planning for operator interfacing with access hatch at sea (from support vessel) | 11/01/2020 | Open | 5 | 2 | Med | 10 | 10.4
|  | X.1334.3 | Perform electrical/power system service via electrical service hatch (including communication and software) | Ensure appropriate weather window and safety of equipment from seawater ingress, ensure watertight integrity is maintained by reconstituting watertight seals | 3 | Novel operational procedures | Damage to electrical equipment | Short circuit Incorrect electrical system changes since previous connection | SCADA | Repair needed on WEC Cost and program delay | Electrical testing SOP Electrical safety SOP | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 10.4
| X.1400 |  | Disconnecting umblilical | [16 empty] | open
|  | X.1410.1 | Disconnect umbilical | Verify system is deenergized and disconnect connector | 2 | Novel electrical system & operational procedures | Electric shock | Improper electrical safety Improper wiring | Safety observer | Human safety | Electrical testing SOP Electrical safety SOP | 5 | 2 | Med | 10 |  | Detailed install procedures Perform HAZID with local operators prior to any operations | Operations plans reviewed with offshore partners. HAZID will be performed with local operators shortly before operations. | 8/15/2020 | Closed | 5 | 2 | Med | 10 | 10.6
|  | X.1410.2 | Disconnect umbilical | Verify system is deenergized and disconnect connector | 2 | Novel electrical system & operational procedures | Damage to electrical equipment | Short circuit Incorrect electrical system changes since previous connection | SCADA | Repair needed on WEC Cost and program delay | Electrical testing SOP Electrical safety SOP | 4 | 3 | Med | 12 |  | Detailed install procedures Perform HAZID with local operators prior to any operations | Operations plans reviewed with offshore partners. HAZID will be performed with local operators shortly before operations. | 8/15/2020 | Closed | 4 | 2 | Med | 8 | 10.6
|  | X.1420.1 | Retrieve umbilical | Pickup umbilical for connection | 2 | Novel electrical system & operational procedures | Pickup buoy off station | Hardware failure Human error (not securring pin, etc) | Visual inspection | Cost and program delay (required dive operation to retrieve) | Review operational planning vessel operators | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 10.6
|  | X.1420.2 | Retrieve umbilical | Pickup umbilical for connection | 2 | Novel electrical system & operational procedures | Damage to umbilical during operation | Abraision Contact with vessel or subsea equipment | Drop camera | Cost and program delay | Review operational planning vessel operators Use cable protection where appropriate | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 10.6
|  | X.1420.3 | Retrieve umbilical | Pickup umbilical for connection | 2 | Novel electrical system & operational procedures | Exceed minimum bend radius during operation | Lay plan does not adequatly consider lay angles Vessel does not adequatly follow lay plan | Vessel GPS Drop camera | Damage to umbilical | Review operational planning with vessel operators Use cable protection where appropriate | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 10.6
|  | X.1420.4 | Retrieve umbilical | Pickup umbilical for connection | 2 | Novel electrical system & operational procedures | Damage to vessel | Umbilical comes up into propeller | Drop camera | Cost and program delay | Plan for drop camera use during operation Review operational planning with vessel operators | 4 | 2 | Med | 8 |  | Detailed install procedures Perform HAZID with local operators prior to any operations | Operations plans reviewed with offshore partners. HAZID will be performed with local operators shortly before operations. | 8/15/2020 | Closed | 4 | 2 | Med | 8 | 10.6
|  | X.1420.5 | Retrieve umbilical | Pickup umbilical for connection | 2 | Novel electrical system & operational procedures | Entaglement with other subsea infrastructure and/or lines | Insufficient touchdown anchor Excessive wave loading Unanticipated subsea dynamics | Drop camera | Damage to umbilical Damage to other subsea infrastructure | Seafloor survey prior to cable lay Plan for drop camera use during operation Review operational planning with vessel operators | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 10.6
| X.1500 |  | Disconnecting mooring lines from PTO | [16 empty] | open
|  | X.1510.1 | Release tension from mooring lines to allow for disconnection from tender or RIB | Use device controls to release tension on all mooring lines, disconnect one by one | 2 | Device controls | Inability to safely recover WEC | Insufficient weather window | Mooring loads | Project delays and/or WEC damage | SOP to determine appropriate weather windows for maintenance activities | 3 | 2 | Low | 6 |  | Ensure adequate safety margin included in SOP |  | N/A | Closed | 3 | 2 | Low | 6 | 10.5
|  | X.1520.1 | Disconnect mooring line from winch belt | For demo scale, connect from RIB with standard shackle or similiar | 2 | Mooring system connections & novel operational procedures | Mooring line disconnects from bridal | Inadequatly secured hardware Excessive weather with moorings in place, prior to connecting to WEC (no tension on moorings) Human error (dropped hardware) Working from small vessel | Visual inspection | Delay Potential damage to mooring line | Detailed and reviewed installation plan Qualified personnel for working offshore | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 10.5
|  | X.1520.2 | Disconnect mooring line from winch belt | For demo scale, connect from RIB with standard shackle or similiar | 2 | Mooring system connections & novel operational procedures | Personnel safety working offshore | Pinch points between vessel and WEC Potential for man overboard Slips, trips, falls | Safety SOP | Human safety | Safety SOP Only qualified personnel working offshore | 5 | 2 | Med | 10 |  | Detailed install procedures Perform HAZID with local operators prior to any operations | Operations plans reviewed with offshore partners. HAZID will be performed with local operators shortly before operations. | 8/15/2020 | Closed | 5 | 2 | Med | 10 | 10.5
|  | X.1520.3 | Disconnect mooring line from winch belt | For demo scale, connect from RIB with standard shackle or similiar | 2 | Mooring system connections & novel operational procedures | Vessel contact with WEC | Inadequate design or plan for connection Wave/wind loads during operation Abrupt vessel movement | Installation plan | Damage to WEC Damage to vessel | Review installation plan with vessel operators Place vessel on windward side of WEC to reduce wind/wave loads on WEC | 4 | 2 | Med | 8 |  | Detailed install procedures Perform HAZID with local operators prior to any operations | Operations plans reviewed with offshore partners. HAZID will be performed with local operators shortly before operations. | 8/15/2020 | Closed | 4 | 2 | Med | 8 | 10.5
|  | X.1530.1 | Attach mooring line to bouy | With device alongside vessel, use tender (RIB) to retrive first mooring line and bring to connection point | 1 | None | Mooring line disconnects from bridal | Inadequatly secured hardware Excessive weather with moorings in place, prior to connecting to WEC (no tension on moorings) Human error (dropped hardware) Working from small vessel | Visual inspection | Delay Potential damage to mooring line | Detailed and reviewed installation plan Qualified personnel for working offshore | 3 | 2 | Low | 6 |  |  |  | N/A | Closed | 3 | 2 | Low | 6 | 10.5
|  | X.1530.2 | Attach mooring line to buoy | With device alongside vessel, use tender (RIB) to retrive first mooring line and bring to connection point | 1 | None | Personnel safety working offshore | Pinch points between vessel and buoy Potential for man overboard Slips, trips, falls | Safety SOP | Human safety | Safety SOP Only qualified personnel working offshore | 5 | 2 | Med | 10 |  | Detailed install procedures Perform HAZID with local operators prior to any operations | Operations plans reviewed with offshore partners. HAZID will be performed with local operators shortly before operations. | 8/15/2020 | Closed | 5 | 2 | Med | 10 | 10.5
| X.1600 |  | Towing device to harbor | [16 empty] | open
|  | X.1610 | Same procedure as 0500 | [21 empty] | 10.5
| X.1700 |  | Loss of communication actions | [16 empty] | open
|  | X.1710.1 | Loss of communication inside WEC (WEC internal systems & controls loss of communication) | Novel device | 3 | Controls system | Communications connection, service, or equipment failure | Climate control (temp, humidity), equipment failure | SCADA | Loss of ability to control load mitigation mechanisms | Design load mitigation mechanisms to have "normally safe" operating points when control system is lost. | 3 | 3 | Med | 9 | A minimum threshold remains that cannot be mitigated if control system is lost. | Determine options for inherent safety of design on loss of communications | Controls implimentations and loss of communications strategies to be tested prior to deployment. Fail safe mechanical design of load management mechanisms | 11/01/2020 | Open | 3 | 3 | Med | 9 | 10.4
| X.1800 |  | Loss of power actions | [16 empty] | open
|  | X.1810 | Loss of power on-board WEC | Novel device | 3 | Controls system | Communications connection, service, or equipment failure Prolonged low sea states | Electrical fault resulting in circuit breaker trip (not remotely resetable) Failure of drive | SCADA | Loss of ability to control unpowered system (PTO or hatch actuation) | PTO electrical systems independent from each other such that electrical fault or loss of power with one PTO (or hatch control) should not cascade into loss of power to multiple systems On-board battery capacity sized for contingency Design failsafes for loss of power situation | 3 | 3 | Med | 9 |  | Determine options for inherent safety of design on loss of communications | Controls implimentations and loss of communications strategies to be tested prior to deployment. | 11/01/2020 | Open | 3 | 3 | Med | 9 | 10.4
| X.1900 |  | Loss of one PTO actions | [16 empty] | open
|  | X.1910 | Transition to lower position in water column with increased tension on remaining operational PTOs | Same procedure as 0820 but torque requirements on motor higher | 3 | Controls system | Single PTO system failed offline | Motor/Generator failure Winch or shaft failure Mooring line disconnected | SCADA Mooring line tension | Loss of control of one PTO | Mooring line length and motor specificatied for single failed PTO operations | 4 | 3 | Med | 12 | Modelling has shown that on loss of one PTO the opposite PTO will lose tension, this is the case for both a freewheeling winch drum or locked winch shaft - in either situation WEC shall dive to survival depth (X.1911) until recovery is possible. | Verfiy ability to submerge to survival depth with 3 active PTOs | Winching to survival with loss of one PTO to be validated on bench test in BP2 - with final PTO architecture/configuration | 11/01/2020 | Open | 4 | 3 | Med | 12 | 10.4
[15 empty] | 0 | [8 empty] | 0

## Guidelines & Instructions
Aim of the process
The Failure Mode and Effects Analysis (FMEA) is a qualitative reliability technique for systematically analysing each possible failure mode within a hardware system, and identifying the resulting effect on that system, the mission and personnel. The criticality analysis (CA) is a quantitative procedure which ranks failure modes according to their probability and consequences (i.e. the resulting effect of the failure mode on system, mission or personnel).
Process inputs
The Technology assessment process shall be carried out based on (but not limited to) the following documents. They shall be subsequently provided to DNV for validation of the process
| Input 1 | Certification basis
| Input 2 | Technology assessment
| Input 3 | Detailed drawings of items subject to qualification
| Input 4 | Drawings and descriptions of control and safety systems
| Input 5 | Material specifications
| Input 6 | Outline fabrication procedures
| Input 7 | Outline installation procedures
| Input 8 | Outline inspection and maintenance procedures
Process outputs
This work shall bring a better understanding of the considered system, and put emphasis on the areas on which a detailed description of failures modes and mechanisms is expected in the subsequent process (Failure Mode Identification and Risk Ranking)
| Output 1 | The FMEA process shall result in completion of the enclosed worksheet 'Phases and activities'.
| Output 2 | The FMEA process shall result in completion of the enclosed worksheet 'Components and functions'.
| Output 3 | The FMEA process shall result in completion of the enclosed worksheet 'Supporting documents'. All non-DNV documents supporting statments in Output 1 and Output 2 shall be referenced in this worksheet, and made available to DNV.
Process steps
| Step 1 | Population of the "Component", "Activity", "Tech class" and "Function" columns of the spreadsheets "Components and functions" and Phases and activities" spreadsheets
| Step 2 | Determination of probability and consequence classes and definition of the risk matrix
FOR each component
FOR each life cycle phase
| Step 21 | Identify component's failure modes
FOR each failure mode
| Step 211 | Identify failure mechanism
FOR each failure mechanism
| Step 2111 | Identify consequences classes and probability classes Identify detection process List controls currently implemented to avoid failure mechanism
About the FMEA outputs
| Statement 1 | Different failure modes shall be addressed in different rows as they may have different failure mechanisms
| Statement 2 | Different failure mechanisms shall be addressed in different rows as they may have different risk ranking
| Statement 3 | Relevant combination of failure modes which combined probability higher than NUMBER and combined consequences higher than NUMBER shall be considered
| Statement 4 | Level of detail of failure modes and failure mechanisms shall be high for technologies which risk is equal or higher than 3
| Statement 5 | All controls measures shall be listed, including for instance, quality controls performed by manufacturers
General aspects:
The Failure Mode Identification and Risk Ranking (FMIRR) is based on the Failure Mode and Effects Analysis (FMEA) that is a qualitative reliability technique for systematically analysing each possible failure mode within a hardware system, and identifying the resulting effect on safety, environment, operation and asset. The Risk Ranking is a quantitative procedure which ranks failure modes according to their probability and consequences (i.e. the resulting effect of the failure mode on safety, environment, operation and asset).
The FMIRR process shall be carried out based on (but not limited to) the following documents:
· Certification basis
· Technology assessment
· Detailed drawings of items subject to review
· Drawings and descriptions of control and safety systems
· Material specifications
· Outline fabrication procedures
· Outline installation procedures
· Outline inspection and maintenance procedures
This work shall bring a further understanding of the considered system, and increase emphasis on the areas upon which a detailed description of failures modes and mechanisms is expected in the subsequent process
The consequence and probability classes as well as the risk matrix are defined in Set-up
Steps
The information from the Technology Assessment together with the breakdown of technology (and technology class) as well as any novel aspects is used as the starting point for the FMIRR.
The failure modes are identified to the level required by the technology class and by addressing the novel aspects identified. The failure mechanisms are listed with focus on the aspects affected by the novel aspects and uncertainties.
Possible early detection of failures should be identified where possible, as the capacity to detect early failures with high probability (and an unequivocal relationship between signal and failure) will influence the definition of the consequences of failure. Detection may in some cases be related to the early stages of failure, or may be related to the development of a mechanism that will lead to subsequent failure.
For the description of consequence, the worst consequence is considered and listed. Consequences should consider any impact on the safety, environment, operation and asset aspects.
Before defining the consequence class for the failure mode, the current controls embedded into the design philosophy and implied in the standards adopted (i.e. redundancy, increased safety level, higher margins, additional proof tests, enhanced fabrication methods and increase levels of NDE), are identified and its impact on the consequence class considered.
The probability of the event is addressed based upon the existing reliability database or upon implied probabilities of failure from the standards adopted. The impact of the novelty is to be taken into account, and the uncertainty is to be added to any relevant information from other industries or any limited experience from the technology developer.
Assumptions and other aspects considered in the process need to be included and considered during the next stages, including design, fabrication, commissioning and in-service life.
For risks identified as “medium” or “high”, recommendations are to be derived in order to reduce the consequence or the probability (or both) in demonstrating that the overall level of the risk has been lessened.
Recommended actions should be assigned to an individual who is responsible for the execution and reporting of that action. They should also hold responsibility for the updating of the FMIRR in recording the impact of that action. After evaluation of the results, re-ranking of the risk can be performed. Where a risk remains high, further action is required to be defined and the FMIRR cycle repeated with the updated information.
Data from the in-service life is to be used as a way to re-evaluate the FMIRR and its conclusions.
Observations:
· The methodology considers one failure at time. However, when one failure can be connected to another failure (i.e. the probability is not affected by the two events), the two failures should be considered in the ultimate consequence assessment. Time delay between events may be considered, and may reduce the consequence by stopping operation before the second failure occurs.
· Where probability of failure is uncertain, emphasis should be given to consequences when recommending actions (e.g. one of the actions in this case could be to obtain more data to reduce uncertainty in the probability of failures before committing to serial production).
· Different failure modes shall be addressed in different rows (as they may have different failure mechanisms).
· Different failure mechanisms shall be addressed in different rows (as they may have a different risk ranking).
· Level of detail of failure modes and failure mechanisms shall be increased for technologies where risk is equal to or higher than 3.
· All controls measures shall be listed, including quality controls performed by manufacturers.

## Supporting documents
CalWave Ocean Demonstration
CalWave Scale System
Documentation used
Doc. No. | Title | Rev. | Observations/comments | Date
1 | MEC Certification Basis | 2 | Supporting document to Technology Assessment developed in collaboration with DNV | 2018-05-21
2 | Technology Assessment | 2 | Supporting document to FMECA developed in collaboration with DNV | 2018-09-27
3 | FMECA | 4 | Developed in collaboration with NREL, DNV & partners | 2019-05-30
4 | Project Management Plan | 4 | Foundational project document | 2017-12-28
5 | HSE Plan | 1 | Developed in collaboration with DelMar | 2018-09-17
6 | MOC Plan | 1 | Developed in collaboration with DelMar | 2018-09-17
7 | NREL Risk Management Report | 3 | Summary of NREL support for risk management | 2019-05-17